## Power and Disinfectant
Energy Calculations for a system using Ozone Disinfection |  |  |  |  | Pump Efficiency | 72% | [ % ] | Contact Time | 10 | [min] | UV Lamp Size | 50 | [W] | Heating Value Diesel | 40 | [MJ/L]
Catch. Area | 100 | [m2] |  |  | MTBF | 1650 |  | Ct_Ozone | 50 | [mg min/L] |  | 40 LPM | [Wh] | Efficiency of Generator | 35% | [ % ]
Catch. Tank V | 2.5 | [m3] |  |  | Maintainance | 0.11672 | per 5 years | Energy for O3 | 2 | [MJ / g]
Consumption | 450 | [L/day] | [10 empty] | Energy not used for first month |  | Cost of Fuel |  |  | Cost of oil | 100 | CO2 Emmissions | Shipping CO2 Emmissions | Minimum | Maximum
Initial Volume | 0 | [L] | [10 empty] | 0 |  | 4971.8274 |  |  | Maintainance | 7 | [kg/5 years] | [kg/5 years]
SUM -> |  | 1155550 |  |  |  |  | 121.9747 |  | 2311.1 |  | 4622.2 |  | 3019.68 | 7763.8547 | 1420.5221 |  |  | 2 | 5 | 15439.7422 | 21185.6875 | 3177.8531 | 22244.9719
Day | Rain | Qin | Consumption | Stored Water | Pump Pressure | Pump Energy | Pump Energy | Mass O3 | Mass O3 | Energy for O3 | Energy for O3 | Energy for UV | Energy for UV | Total Energy for Day | Diesel Fuel | Amount of time since the oil change [days] | Amount of time since refuleing [days] | Oil Changes | Refueling | Satisfaction
[ date ] | [mm] | [m3] | [m3] | [m3] | [Pa] | [J] | [MJ] | [mg] | [g] | [J] | [MJ] | [Wh] | [MJ] | [MJ] | [L] |  |  |  |  | 28.27%
2014-01-01 | 18.8 | 1.88 | 0 | 1.88 | 190000 | 496111.1111 | 0.49611 | 9400 | 9.4 | 18800000 | 18.8 | 0 | 0 | 19.2961 | 1.3783 | 1.3783 | 1.3783 | 0 | 0
2014-01-02 | 19.8 | 1.98 | 0 | 3.86 | 190000 | 522500 | 0.5225 | 9900 | 9.9 | 19800000 | 19.8 | 0 | 0 | 20.3225 | 1.4516 | 2.8299 | 2.8299 | 0 | 0
2014-01-03 | 0 | 0 | 0 | 3.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8299 | 2.8299 | 0 | 0
2014-01-04 | 0 | 0 | 0 | 3.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8299 | 2.8299 | 0 | 0
2014-01-05 | 0 | 0 | 0 | 3.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8299 | 2.8299 | 0 | 0
2014-01-06 | 5 | 0.5 | 0 | 4.36 | 190000 | 131944.4444 | 0.13194 | 2500 | 2.5 | 5000000 | 5 | 0 | 0 | 5.1319 | 0.36657 | 3.1965 | 3.1965 | 0 | 0
2014-01-07 | 20.4 | 2.04 | 0 | 6.4 | 190000 | 538333.3333 | 0.53833 | 10200 | 10.2 | 20400000 | 20.4 | 0 | 0 | 20.9383 | 1.4956 | 4.6921 | 4.6921 | 0 | 0
2014-01-08 | 24.8 | 2.48 | 0 | 8.88 | 190000 | 654444.4444 | 0.65444 | 12400 | 12.4 | 24800000 | 24.8 | 0 | 0 | 25.4544 | 1.8182 | 6.5102 | 6.5102 | 0 | 0
2014-01-09 | 34 | 2.5 | 0 | 11.38 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 0 | 0 | 25.6597 | 1.8328 | 8.3431 | 8.3431 | 0 | 0
2014-01-10 | 44.6 | 2.5 | 0 | 13.88 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 0 | 0 | 25.6597 | 1.8328 | 10.1759 | 10.1759 | 0 | 0
2014-01-11 | 14.4 | 1.44 | 0 | 15.32 | 190000 | 380000 | 0.38 | 7200 | 7.2 | 14400000 | 14.4 | 0 | 0 | 14.78 | 1.0557 | 11.2316 | 11.2316 | 0 | 0
2014-01-12 | 50.2 | 2.5 | 0 | 17.82 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 0 | 0 | 25.6597 | 1.8328 | 13.0645 | 13.0645 | 0 | 0
2014-01-13 | 9.6 | 0.96 | 0 | 18.78 | 190000 | 253333.3333 | 0.25333 | 4800 | 4.8 | 9600000 | 9.6 | 0 | 0 | 9.8533 | 0.70381 | 13.7683 | 13.7683 | 0 | 0
2014-01-14 | 5.8 | 0.58 | 0 | 19.36 | 190000 | 153055.5556 | 0.15306 | 2900 | 2.9 | 5800000 | 5.8 | 0 | 0 | 5.9531 | 0.42522 | 14.1935 | 14.1935 | 0 | 0
2014-01-15 | 1.6 | 0.16 | 0 | 19.52 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 0 | 0 | 1.6422 | 0.1173 | 14.3108 | 14.3108 | 0 | 0
2014-01-16 | 0.8 | 0.08 | 0 | 19.6 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 0 | 0 | 0.82111 | 0.058651 | 14.3694 | 14.3694 | 0 | 0
2014-01-17 | 0 | 0 | 0 | 19.6 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3694 | 14.3694 | 0 | 0
2014-01-18 | 2.6 | 0.26 | 0 | 19.86 | 190000 | 68611.1111 | 0.068611 | 1300 | 1.3 | 2600000 | 2.6 | 0 | 0 | 2.6686 | 0.19062 | 14.5601 | 14.5601 | 0 | 0
2014-01-19 | 1 | 0.1 | 0 | 19.96 | 190000 | 26388.8889 | 0.026389 | 500 | 0.5 | 1000000 | 1 | 0 | 0 | 1.0264 | 0.073313 | 14.6334 | 14.6334 | 0 | 0
2014-01-20 | 0.6 | 0.06 | 0 | 20.02 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 0 | 0 | 0.61583 | 0.043988 | 14.6774 | 14.6774 | 0 | 0
2014-01-21 | 0.8 | 0.08 | 0 | 20.1 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 0 | 0 | 0.82111 | 0.058651 | 14.736 | 14.736 | 0 | 0
2014-01-22 | 0.6 | 0.06 | 0 | 20.16 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 0 | 0 | 0.61583 | 0.043988 | 14.78 | 14.78 | 0 | 0
2014-01-23 | 0 | 0 | 0 | 20.16 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.78 | 14.78 | 0 | 0
2014-01-24 | 0 | 0 | 0 | 20.16 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.78 | 14.78 | 0 | 0
2014-01-25 | 0 | 0 | 0 | 20.16 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.78 | 14.78 | 0 | 0
2014-01-26 | 0 | 0 | 0 | 20.16 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.78 | 14.78 | 0 | 0
2014-01-27 | 17.6 | 1.76 | 0 | 21.92 | 190000 | 464444.4444 | 0.46444 | 8800 | 8.8 | 17600000 | 17.6 | 0 | 0 | 18.0644 | 1.2903 | 16.0703 | 16.0703 | 0 | 0
2014-01-28 | 0 | 0 | 0 | 21.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0703 | 16.0703 | 0 | 0
2014-01-29 | 0 | 0 | 0 | 21.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0703 | 16.0703 | 0 | 0
2014-01-30 | 0 | 0 | 0 | 21.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.0703 | 16.0703 | 0 | 0
2014-01-31 | 2.6 | 0.26 | 0 | 22.18 | 190000 | 68611.1111 | 0.068611 | 1300 | 1.3 | 2600000 | 2.6 | 0 | 0 | 2.6686 | 0.19062 | 16.2609 | 16.2609 | 0 | 0
2014-02-01 | 2.6 | 0.26 | 0.45 | 21.99 | 190000 | 68611.1111 | 0.068611 | 1300 | 1.3 | 2600000 | 2.6 | 1200 | 4.32 | 6.9886 | 0.49919 | 16.7601 | 16.7601 | 0 | 0
2014-02-02 | 0 | 0 | 0.45 | 21.54 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 17.0687 | 17.0687 | 0 | 0
2014-02-03 | 0 | 0 | 0.45 | 21.09 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 17.3773 | 17.3773 | 0 | 0
2014-02-04 | 0 | 0 | 0.45 | 20.64 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 17.6858 | 17.6858 | 0 | 0
2014-02-05 | 0 | 0 | 0.45 | 20.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 17.9944 | 17.9944 | 0 | 0
2014-02-06 | 0 | 0 | 0.45 | 19.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 18.303 | 18.303 | 0 | 0
2014-02-07 | 0 | 0 | 0.45 | 19.29 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 18.6115 | 18.6115 | 0 | 0
2014-02-08 | 0 | 0 | 0.45 | 18.84 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 18.9201 | 18.9201 | 0 | 0
2014-02-09 | 12.2 | 1.22 | 0.45 | 19.61 | 190000 | 321944.4444 | 0.32194 | 6100 | 6.1 | 12200000 | 12.2 | 1200 | 4.32 | 16.8419 | 1.203 | 20.1231 | 20.1231 | 0 | 0
2014-02-10 | 13.4 | 1.34 | 0.45 | 20.5 | 190000 | 353611.1111 | 0.35361 | 6700 | 6.7 | 13400000 | 13.4 | 1200 | 4.32 | 18.0736 | 1.291 | 21.4141 | 21.4141 | 0 | 0
2014-02-11 | 46.6 | 2.5 | 0.45 | 22.55 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 23.5555 | 23.5555 | 0 | 0
2014-02-12 | 16.8 | 1.68 | 0.45 | 23.78 | 190000 | 443333.3333 | 0.44333 | 8400 | 8.4 | 16800000 | 16.8 | 1200 | 4.32 | 21.5633 | 1.5402 | 25.0957 | 25.0957 | 0 | 0
2014-02-13 | 15.6 | 1.56 | 0.45 | 24.89 | 190000 | 411666.6667 | 0.41167 | 7800 | 7.8 | 15600000 | 15.6 | 1200 | 4.32 | 20.3317 | 1.4523 | 26.548 | 26.548 | 0 | 0
2014-02-14 | 3 | 0.3 | 0.45 | 24.74 | 190000 | 79166.6667 | 0.079167 | 1500 | 1.5 | 3000000 | 3 | 1200 | 4.32 | 7.3992 | 0.52851 | 27.0765 | 27.0765 | 0 | 0
2014-02-15 | 11.6 | 1.16 | 0.45 | 25.45 | 190000 | 306111.1111 | 0.30611 | 5800 | 5.8 | 11600000 | 11.6 | 1200 | 4.32 | 16.2261 | 1.159 | 28.2355 | 28.2355 | 0 | 0
2014-02-16 | 19 | 1.9 | 0.45 | 26.9 | 190000 | 501388.8889 | 0.50139 | 9500 | 9.5 | 19000000 | 19 | 1200 | 4.32 | 23.8214 | 1.7015 | 29.937 | 29.937 | 0 | 0
2014-02-17 | 9.2 | 0.92 | 0.45 | 27.37 | 190000 | 242777.7778 | 0.24278 | 4600 | 4.6 | 9200000 | 9.2 | 1200 | 4.32 | 13.7628 | 0.98306 | 30.9201 | 30.9201 | 0 | 0
2014-02-18 | 12.6 | 1.26 | 0.45 | 28.18 | 190000 | 332500 | 0.3325 | 6300 | 6.3 | 12600000 | 12.6 | 1200 | 4.32 | 17.2525 | 1.2323 | 32.1524 | 32.1524 | 0 | 0
2014-02-19 | 21.8 | 2.18 | 0.45 | 29.91 | 190000 | 575277.7778 | 0.57528 | 10900 | 10.9 | 21800000 | 21.8 | 1200 | 4.32 | 26.6953 | 1.9068 | 34.0592 | 34.0592 | 0 | 0
2014-02-20 | 2.4 | 0.24 | 0.45 | 29.7 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 34.5438 | 34.5438 | 0 | 0
2014-02-21 | 0.8 | 0.08 | 0.45 | 29.33 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 34.911 | 34.911 | 0 | 0
2014-02-22 | 4.8 | 0.48 | 0.45 | 29.36 | 190000 | 126666.6667 | 0.12667 | 2400 | 2.4 | 4800000 | 4.8 | 1200 | 4.32 | 9.2467 | 0.66048 | 35.5714 | 35.5714 | 0 | 0
2014-02-23 | 14.6 | 1.46 | 0.45 | 30.37 | 190000 | 385277.7778 | 0.38528 | 7300 | 7.3 | 14600000 | 14.6 | 1200 | 4.32 | 19.3053 | 1.3789 | 36.9504 | 36.9504 | 0 | 0
2014-02-24 | 6.8 | 0.68 | 0.45 | 30.6 | 190000 | 179444.4444 | 0.17944 | 3400 | 3.4 | 6800000 | 6.8 | 1200 | 4.32 | 11.2994 | 0.8071 | 37.7575 | 37.7575 | 0 | 0
2014-02-25 | 0 | 0 | 0.45 | 30.15 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 38.0661 | 38.0661 | 0 | 0
2014-02-26 | 0.8 | 0.08 | 0.45 | 29.78 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 38.4333 | 38.4333 | 0 | 0
2014-02-27 | 0 | 0 | 0.45 | 29.33 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 38.7419 | 38.7419 | 0 | 0
2014-02-28 | 0.4 | 0.04 | 0.45 | 28.92 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 39.0798 | 39.0798 | 0 | 0
2014-03-01 | 2 | 0.2 | 0.45 | 28.67 | 190000 | 52777.7778 | 0.052778 | 1000 | 1 | 2000000 | 2 | 1200 | 4.32 | 6.3728 | 0.4552 | 39.535 | 39.535 | 0 | 0
2014-03-02 | 19 | 1.9 | 0.45 | 30.12 | 190000 | 501388.8889 | 0.50139 | 9500 | 9.5 | 19000000 | 19 | 1200 | 4.32 | 23.8214 | 1.7015 | 41.2365 | 41.2365 | 0 | 0
2014-03-03 | 1 | 0.1 | 0.45 | 29.77 | 190000 | 26388.8889 | 0.026389 | 500 | 0.5 | 1000000 | 1 | 1200 | 4.32 | 5.3464 | 0.38188 | 41.6184 | 41.6184 | 0 | 0
2014-03-04 | 2.4 | 0.24 | 0.45 | 29.56 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 42.1029 | 42.1029 | 0 | 0
2014-03-05 | 23.8 | 2.38 | 0.45 | 31.49 | 190000 | 628055.5556 | 0.62806 | 11900 | 11.9 | 23800000 | 23.8 | 1200 | 4.32 | 28.7481 | 2.0534 | 44.1563 | 44.1563 | 0 | 0
2014-03-06 | 8.6 | 0.86 | 0.45 | 31.9 | 190000 | 226944.4444 | 0.22694 | 4300 | 4.3 | 8600000 | 8.6 | 1200 | 4.32 | 13.1469 | 0.93907 | 45.0954 | 45.0954 | 0 | 0
2014-03-07 | 34 | 2.5 | 0.45 | 33.95 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 47.2368 | 47.2368 | 0 | 0
2014-03-08 | 52.4 | 2.5 | 0.45 | 36 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 49.3782 | 49.3782 | 0 | 0
2014-03-09 | 10.6 | 1.06 | 0.45 | 36.61 | 190000 | 279722.2222 | 0.27972 | 5300 | 5.3 | 10600000 | 10.6 | 1200 | 4.32 | 15.1997 | 1.0857 | 50.4639 | 50.4639 | 0 | 0
2014-03-10 | 2.4 | 0.24 | 0.45 | 36.4 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 50.9484 | 50.9484 | 0 | 0
2014-03-11 | 0 | 0 | 0.45 | 35.95 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 51.257 | 51.257 | 0 | 0
2014-03-12 | 2.8 | 0.28 | 0.45 | 35.78 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 51.7709 | 51.7709 | 0 | 0
2014-03-13 | 20.2 | 2.02 | 0.45 | 37.35 | 190000 | 533055.5556 | 0.53306 | 10100 | 10.1 | 20200000 | 20.2 | 1200 | 4.32 | 25.0531 | 1.7895 | 53.5604 | 53.5604 | 0 | 0
2014-03-14 | 13.8 | 1.38 | 0.45 | 38.28 | 190000 | 364166.6667 | 0.36417 | 6900 | 6.9 | 13800000 | 13.8 | 1200 | 4.32 | 18.4842 | 1.3203 | 54.8807 | 54.8807 | 0 | 0
2014-03-15 | 22.8 | 2.28 | 0.45 | 40.11 | 190000 | 601666.6667 | 0.60167 | 11400 | 11.4 | 22800000 | 22.8 | 1200 | 4.32 | 27.7217 | 1.9801 | 56.8608 | 56.8608 | 0 | 0
2014-03-16 | 5.4 | 0.54 | 0.45 | 40.2 | 190000 | 142500 | 0.1425 | 2700 | 2.7 | 5400000 | 5.4 | 1200 | 4.32 | 9.8625 | 0.70446 | 57.5652 | 57.5652 | 0 | 0
2014-03-17 | 0.4 | 0.04 | 0.45 | 39.79 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 57.9031 | 57.9031 | 0 | 0
2014-03-18 | 31 | 2.5 | 0.45 | 41.84 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 60.0445 | 60.0445 | 0 | 0
2014-03-19 | 1.6 | 0.16 | 0.45 | 41.55 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 60.4704 | 60.4704 | 0 | 0
2014-03-20 | 1.6 | 0.16 | 0.45 | 41.26 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 60.8963 | 60.8963 | 0 | 0
2014-03-21 | 7.6 | 0.76 | 0.45 | 41.57 | 190000 | 200555.5556 | 0.20056 | 3800 | 3.8 | 7600000 | 7.6 | 1200 | 4.32 | 12.1206 | 0.86575 | 61.762 | 61.762 | 0 | 0
2014-03-22 | 2.6 | 0.26 | 0.45 | 41.38 | 190000 | 68611.1111 | 0.068611 | 1300 | 1.3 | 2600000 | 2.6 | 1200 | 4.32 | 6.9886 | 0.49919 | 62.2612 | 62.2612 | 0 | 0
2014-03-23 | 0 | 0 | 0.45 | 40.93 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 62.5698 | 62.5698 | 0 | 0
2014-03-24 | 4 | 0.4 | 0.45 | 40.88 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 63.1716 | 63.1716 | 0 | 0
2014-03-25 | 31 | 2.5 | 0.45 | 42.93 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 65.313 | 65.313 | 0 | 0
2014-03-26 | 0.2 | 0.02 | 0.45 | 42.5 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 65.6363 | 65.6363 | 0 | 0
2014-03-27 | 4.4 | 0.44 | 0.45 | 42.49 | 190000 | 116111.1111 | 0.11611 | 2200 | 2.2 | 4400000 | 4.4 | 1200 | 4.32 | 8.8361 | 0.63115 | 66.2674 | 66.2674 | 0 | 0
2014-03-28 | 23.6 | 2.36 | 0.45 | 44.4 | 190000 | 622777.7778 | 0.62278 | 11800 | 11.8 | 23600000 | 23.6 | 1200 | 4.32 | 28.5428 | 2.0388 | 68.3062 | 68.3062 | 0 | 0
2014-03-29 | 41.6 | 2.5 | 0.45 | 46.45 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 70.4476 | 70.4476 | 0 | 0
2014-03-30 | 3 | 0.3 | 0.45 | 46.3 | 190000 | 79166.6667 | 0.079167 | 1500 | 1.5 | 3000000 | 3 | 1200 | 4.32 | 7.3992 | 0.52851 | 70.9761 | 70.9761 | 0 | 0
2014-03-31 | 0 | 0 | 0.45 | 45.85 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 71.2847 | 71.2847 | 0 | 0
2014-04-01 | 0 | 0 | 0.45 | 45.4 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 71.5933 | 71.5933 | 0 | 0
2014-04-02 | 5.6 | 0.56 | 0.45 | 45.51 | 190000 | 147777.7778 | 0.14778 | 2800 | 2.8 | 5600000 | 5.6 | 1200 | 4.32 | 10.0678 | 0.71913 | 72.3124 | 72.3124 | 0 | 0
2014-04-03 | 20.4 | 2.04 | 0.45 | 47.1 | 190000 | 538333.3333 | 0.53833 | 10200 | 10.2 | 20400000 | 20.4 | 1200 | 4.32 | 25.2583 | 1.8042 | 74.1165 | 74.1165 | 0 | 0
2014-04-04 | 2.6 | 0.26 | 0.45 | 46.91 | 190000 | 68611.1111 | 0.068611 | 1300 | 1.3 | 2600000 | 2.6 | 1200 | 4.32 | 6.9886 | 0.49919 | 74.6157 | 74.6157 | 0 | 0
2014-04-05 | 15.9 | 1.59 | 0.45 | 48.05 | 190000 | 419583.3333 | 0.41958 | 7950 | 7.95 | 15900000 | 15.9 | 1200 | 4.32 | 20.6396 | 1.4743 | 76.09 | 76.09 | 0 | 0
2014-04-06 | 9.4 | 0.94 | 0.45 | 48.54 | 190000 | 248055.5556 | 0.24806 | 4700 | 4.7 | 9400000 | 9.4 | 1200 | 4.32 | 13.9681 | 0.99772 | 77.0877 | 77.0877 | 0 | 0
2014-04-07 | 13.6 | 1.36 | 0.45 | 49.45 | 190000 | 358888.8889 | 0.35889 | 6800 | 6.8 | 13600000 | 13.6 | 1200 | 4.32 | 18.2789 | 1.3056 | 78.3933 | 78.3933 | 0 | 0
2014-04-08 | 5.6 | 0.56 | 0.45 | 49.56 | 190000 | 147777.7778 | 0.14778 | 2800 | 2.8 | 5600000 | 5.6 | 1200 | 4.32 | 10.0678 | 0.71913 | 79.1125 | 79.1125 | 0 | 0
2014-04-09 | 0 | 0 | 0.45 | 49.11 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 79.421 | 79.421 | 0 | 0
2014-04-10 | 16.6 | 1.66 | 0.45 | 50.32 | 190000 | 438055.5556 | 0.43806 | 8300 | 8.3 | 16600000 | 16.6 | 1200 | 4.32 | 21.3581 | 1.5256 | 80.9466 | 80.9466 | 0 | 0
2014-04-11 | 0 | 0 | 0.45 | 49.87 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 81.2552 | 81.2552 | 0 | 0
2014-04-12 | 0 | 0 | 0.45 | 49.42 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 81.5638 | 81.5638 | 0 | 0
2014-04-13 | 0 | 0 | 0.45 | 48.97 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 81.8723 | 81.8723 | 0 | 0
2014-04-14 | 14.8 | 1.48 | 0.45 | 50 | 190000 | 390555.5556 | 0.39056 | 7400 | 7.4 | 14800000 | 14.8 | 1200 | 4.32 | 19.5106 | 1.3936 | 83.2659 | 83.2659 | 0 | 0
2014-04-15 | 20.8 | 2.08 | 0.45 | 51.63 | 190000 | 548888.8889 | 0.54889 | 10400 | 10.4 | 20800000 | 20.8 | 1200 | 4.32 | 25.6689 | 1.8335 | 85.0994 | 85.0994 | 0 | 0
2014-04-16 | 37.4 | 2.5 | 0.45 | 53.68 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 87.2408 | 87.2408 | 0 | 0
2014-04-17 | 9.8 | 0.98 | 0.45 | 54.21 | 190000 | 258611.1111 | 0.25861 | 4900 | 4.9 | 9800000 | 9.8 | 1200 | 4.32 | 14.3786 | 1.027 | 88.2679 | 88.2679 | 0 | 0
2014-04-18 | 1.9 | 0.19 | 0.45 | 53.95 | 190000 | 50138.8889 | 0.050139 | 950 | 0.95 | 1900000 | 1.9 | 1200 | 4.32 | 6.2701 | 0.44787 | 88.7158 | 88.7158 | 0 | 0
2014-04-19 | 21 | 2.1 | 0.45 | 55.6 | 190000 | 554166.6667 | 0.55417 | 10500 | 10.5 | 21000000 | 21 | 1200 | 4.32 | 25.8742 | 1.8482 | 90.5639 | 90.5639 | 0 | 0
2014-04-20 | 30 | 2.5 | 0.45 | 57.65 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 92.7053 | 92.7053 | 0 | 0
2014-04-21 | 0 | 0 | 0.45 | 57.2 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 93.0139 | 93.0139 | 0 | 0
2014-04-22 | 4.4 | 0.44 | 0.45 | 57.19 | 190000 | 116111.1111 | 0.11611 | 2200 | 2.2 | 4400000 | 4.4 | 1200 | 4.32 | 8.8361 | 0.63115 | 93.645 | 93.645 | 0 | 0
2014-04-23 | 12.8 | 1.28 | 0.45 | 58.02 | 190000 | 337777.7778 | 0.33778 | 6400 | 6.4 | 12800000 | 12.8 | 1200 | 4.32 | 17.4578 | 1.247 | 94.892 | 94.892 | 0 | 0
2014-04-24 | 26 | 2.5 | 0.45 | 60.07 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 97.0334 | 97.0334 | 0 | 0
2014-04-25 | 1.8 | 0.18 | 0.45 | 59.8 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 97.474 | 97.474 | 0 | 0
2014-04-26 | 35 | 2.5 | 0.45 | 61.85 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 99.6154 | 99.6154 | 0 | 0
2014-04-27 | 7.2 | 0.72 | 0.45 | 62.12 | 190000 | 190000 | 0.19 | 3600 | 3.6 | 7200000 | 7.2 | 1200 | 4.32 | 11.71 | 0.83643 | 100.4518 | 0 | 0 | 1
2014-04-28 | 0.8 | 0.08 | 0.45 | 61.75 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 100.819 | 0.36722 | 0 | 0
2014-04-29 | 0.1 | 0.01 | 0.45 | 61.31 | 190000 | 2638.8889 | 0.0026389 | 50 | 0.05 | 100000 | 0.1 | 1200 | 4.32 | 4.4226 | 0.3159 | 101.1349 | 0.68312 | 0 | 0
2014-04-30 | 0 | 0 | 0.45 | 60.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 101.4435 | 0.9917 | 0 | 0
2014-05-01 | 0 | 0 | 0.45 | 60.41 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 101.7521 | 1.3003 | 0 | 0
2014-05-02 | 2 | 0.2 | 0.45 | 60.16 | 190000 | 52777.7778 | 0.052778 | 1000 | 1 | 2000000 | 2 | 1200 | 4.32 | 6.3728 | 0.4552 | 102.2073 | 1.7555 | 0 | 0
2014-05-03 | 4.6 | 0.46 | 0.45 | 60.17 | 190000 | 121388.8889 | 0.12139 | 2300 | 2.3 | 4600000 | 4.6 | 1200 | 4.32 | 9.0414 | 0.64581 | 102.8531 | 2.4013 | 0 | 0
2014-05-04 | 3.8 | 0.38 | 0.45 | 60.1 | 190000 | 100277.7778 | 0.10028 | 1900 | 1.9 | 3800000 | 3.8 | 1200 | 4.32 | 8.2203 | 0.58716 | 103.4402 | 2.9884 | 0 | 0
2014-05-05 | 0 | 0 | 0.45 | 59.65 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 103.7488 | 3.297 | 0 | 0
2014-05-06 | 0 | 0 | 0.45 | 59.2 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 104.0574 | 3.6056 | 0 | 0
2014-05-07 | 0 | 0 | 0.45 | 58.75 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 104.366 | 3.9142 | 0 | 0
2014-05-08 | 0 | 0 | 0.45 | 58.3 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 104.6745 | 4.2227 | 0 | 0
2014-05-09 | 0 | 0 | 0.45 | 57.85 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 104.9831 | 4.5313 | 0 | 0
2014-05-10 | 0.2 | 0.02 | 0.45 | 57.42 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 105.3063 | 4.8545 | 0 | 0
2014-05-11 | 0 | 0 | 0.45 | 56.97 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 105.6149 | 5.1631 | 0 | 0
2014-05-12 | 0.2 | 0.02 | 0.45 | 56.54 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 105.9381 | 5.4863 | 0 | 0
2014-05-13 | 0 | 0 | 0.45 | 56.09 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 106.2467 | 5.7949 | 0 | 0
2014-05-14 | 0 | 0 | 0.45 | 55.64 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 106.5553 | 6.1035 | 0 | 0
2014-05-15 | 0 | 0 | 0.45 | 55.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 106.8639 | 6.4121 | 0 | 0
2014-05-16 | 2.8 | 0.28 | 0.45 | 55.02 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 107.3777 | 6.9259 | 0 | 0
2014-05-17 | 0 | 0 | 0.45 | 54.57 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 107.6863 | 7.2345 | 0 | 0
2014-05-18 | 0 | 0 | 0.45 | 54.12 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 107.9949 | 7.543 | 0 | 0
2014-05-19 | 0 | 0 | 0.45 | 53.67 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 108.3034 | 7.8516 | 0 | 0
2014-05-20 | 0 | 0 | 0.45 | 53.22 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 108.612 | 8.1602 | 0 | 0
2014-05-21 | 8.2 | 0.82 | 0.45 | 53.59 | 190000 | 216388.8889 | 0.21639 | 4100 | 4.1 | 8200000 | 8.2 | 1200 | 4.32 | 12.7364 | 0.90974 | 109.5217 | 9.0699 | 0 | 0
2014-05-22 | 29.6 | 2.5 | 0.45 | 55.64 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 111.6631 | 11.2113 | 0 | 0
2014-05-23 | 0.8 | 0.08 | 0.45 | 55.27 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 112.0304 | 11.5786 | 0 | 0
2014-05-24 | 5.2 | 0.52 | 0.45 | 55.34 | 190000 | 137222.2222 | 0.13722 | 2600 | 2.6 | 5200000 | 5.2 | 1200 | 4.32 | 9.6572 | 0.6898 | 112.7202 | 12.2684 | 0 | 0
2014-05-25 | 23.4 | 2.34 | 0.45 | 57.23 | 190000 | 617500 | 0.6175 | 11700 | 11.7 | 23400000 | 23.4 | 1200 | 4.32 | 28.3375 | 2.0241 | 114.7443 | 14.2925 | 0 | 0
2014-05-26 | 0 | 0 | 0.45 | 56.78 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 115.0528 | 14.601 | 0 | 0
2014-05-27 | 4.4 | 0.44 | 0.45 | 56.77 | 190000 | 116111.1111 | 0.11611 | 2200 | 2.2 | 4400000 | 4.4 | 1200 | 4.32 | 8.8361 | 0.63115 | 115.684 | 15.2322 | 0 | 0
2014-05-28 | 0 | 0 | 0.45 | 56.32 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 115.9926 | 15.5408 | 0 | 0
2014-05-29 | 0 | 0 | 0.45 | 55.87 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 116.3011 | 15.8493 | 0 | 0
2014-05-30 | 0 | 0 | 0.45 | 55.42 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 116.6097 | 16.1579 | 0 | 0
2014-05-31 | 0 | 0 | 0.45 | 54.97 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 116.9183 | 16.4665 | 0 | 0
2014-06-01 | 0 | 0 | 0.45 | 54.52 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 117.2269 | 16.775 | 0 | 0
2014-06-02 | 0 | 0 | 0.45 | 54.07 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 117.5354 | 17.0836 | 0 | 0
2014-06-03 | 0 | 0 | 0.45 | 53.62 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 117.844 | 17.3922 | 0 | 0
2014-06-04 | 0 | 0 | 0.45 | 53.17 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 118.1526 | 17.7008 | 0 | 0
2014-06-05 | 0 | 0 | 0.45 | 52.72 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 118.4611 | 18.0093 | 0 | 0
2014-06-06 | 0 | 0 | 0.45 | 52.27 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 118.7697 | 18.3179 | 0 | 0
2014-06-07 | 0 | 0 | 0.45 | 51.82 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 119.0783 | 18.6265 | 0 | 0
2014-06-08 | 0.2 | 0.02 | 0.45 | 51.39 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 119.4015 | 18.9497 | 0 | 0
2014-06-09 | 0 | 0 | 0.45 | 50.94 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 119.7101 | 19.2583 | 0 | 0
2014-06-10 | 0 | 0 | 0.45 | 50.49 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 120.0187 | 19.5669 | 0 | 0
2014-06-11 | 0 | 0 | 0.45 | 50.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 120.3272 | 19.8754 | 0 | 0
2014-06-12 | 0 | 0 | 0.45 | 49.59 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 120.6358 | 20.184 | 0 | 0
2014-06-13 | 0 | 0 | 0.45 | 49.14 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 120.9444 | 20.4926 | 0 | 0
2014-06-14 | 3.6 | 0.36 | 0.45 | 49.05 | 190000 | 95000 | 0.095 | 1800 | 1.8 | 3600000 | 3.6 | 1200 | 4.32 | 8.015 | 0.5725 | 121.5169 | 21.0651 | 0 | 0
2014-06-15 | 0 | 0 | 0.45 | 48.6 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 121.8254 | 21.3736 | 0 | 0
2014-06-16 | 0 | 0 | 0.45 | 48.15 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 122.134 | 21.6822 | 0 | 0
2014-06-17 | 0 | 0 | 0.45 | 47.7 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 122.4426 | 21.9908 | 0 | 0
2014-06-18 | 1.6 | 0.16 | 0.45 | 47.41 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 122.8685 | 22.4167 | 0 | 0
2014-06-19 | 20.8 | 2.08 | 0.45 | 49.04 | 190000 | 548888.8889 | 0.54889 | 10400 | 10.4 | 20800000 | 20.8 | 1200 | 4.32 | 25.6689 | 1.8335 | 124.702 | 24.2501 | 0 | 0
2014-06-20 | 3.2 | 0.32 | 0.45 | 48.91 | 190000 | 84444.4444 | 0.084444 | 1600 | 1.6 | 3200000 | 3.2 | 1200 | 4.32 | 7.6044 | 0.54317 | 125.2451 | 24.7933 | 0 | 0
2014-06-21 | 1.2 | 0.12 | 0.45 | 48.58 | 190000 | 31666.6667 | 0.031667 | 600 | 0.6 | 1200000 | 1.2 | 1200 | 4.32 | 5.5517 | 0.39655 | 125.6417 | 25.1899 | 0 | 0
2014-06-22 | 0 | 0 | 0.45 | 48.13 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 125.9502 | 25.4984 | 0 | 0
2014-06-23 | 15.4 | 1.54 | 0.45 | 49.22 | 190000 | 406388.8889 | 0.40639 | 7700 | 7.7 | 15400000 | 15.4 | 1200 | 4.32 | 20.1264 | 1.4376 | 127.3878 | 26.936 | 0 | 0
2014-06-24 | 1.2 | 0.12 | 0.45 | 48.89 | 190000 | 31666.6667 | 0.031667 | 600 | 0.6 | 1200000 | 1.2 | 1200 | 4.32 | 5.5517 | 0.39655 | 127.7844 | 27.3326 | 0 | 0
2014-06-25 | 0 | 0 | 0.45 | 48.44 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 128.093 | 27.6412 | 0 | 0
2014-06-26 | 5.8 | 0.58 | 0.45 | 48.57 | 190000 | 153055.5556 | 0.15306 | 2900 | 2.9 | 5800000 | 5.8 | 1200 | 4.32 | 10.2731 | 0.73379 | 128.8268 | 28.375 | 0 | 0
2014-06-27 | 20.4 | 2.04 | 0.45 | 50.16 | 190000 | 538333.3333 | 0.53833 | 10200 | 10.2 | 20400000 | 20.4 | 1200 | 4.32 | 25.2583 | 1.8042 | 130.6309 | 30.1791 | 0 | 0
2014-06-28 | 20.4 | 2.04 | 0.45 | 51.75 | 190000 | 538333.3333 | 0.53833 | 10200 | 10.2 | 20400000 | 20.4 | 1200 | 4.32 | 25.2583 | 1.8042 | 132.4351 | 31.9833 | 0 | 0
2014-06-29 | 0.6 | 0.06 | 0.45 | 51.36 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 132.7876 | 32.3358 | 0 | 0
2014-06-30 | 0 | 0 | 0.45 | 50.91 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 133.0962 | 32.6444 | 0 | 0
2014-07-01 | 0 | 0 | 0.45 | 50.46 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 133.4048 | 32.953 | 0 | 0
2014-07-02 | 1.8 | 0.18 | 0.45 | 50.19 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 133.8453 | 33.3935 | 0 | 0
2014-07-03 | 6.2 | 0.62 | 0.45 | 50.36 | 190000 | 163611.1111 | 0.16361 | 3100 | 3.1 | 6200000 | 6.2 | 1200 | 4.32 | 10.6836 | 0.76312 | 134.6084 | 34.1566 | 0 | 0
2014-07-04 | 9.4 | 0.94 | 0.45 | 50.85 | 190000 | 248055.5556 | 0.24806 | 4700 | 4.7 | 9400000 | 9.4 | 1200 | 4.32 | 13.9681 | 0.99772 | 135.6062 | 35.1544 | 0 | 0
2014-07-05 | 26.6 | 2.5 | 0.45 | 52.9 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 137.7476 | 37.2958 | 0 | 0
2014-07-06 | 13.6 | 1.36 | 0.45 | 53.81 | 190000 | 358888.8889 | 0.35889 | 6800 | 6.8 | 13600000 | 13.6 | 1200 | 4.32 | 18.2789 | 1.3056 | 139.0532 | 38.6014 | 0 | 0
2014-07-07 | 0 | 0 | 0.45 | 53.36 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 139.3618 | 38.91 | 0 | 0
2014-07-08 | 0 | 0 | 0.45 | 52.91 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 139.6703 | 39.2185 | 0 | 0
2014-07-09 | 0 | 0 | 0.45 | 52.46 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 139.9789 | 39.5271 | 0 | 0
2014-07-10 | 0 | 0 | 0.45 | 52.01 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 140.2875 | 39.8357 | 0 | 0
2014-07-11 | 0 | 0 | 0.45 | 51.56 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 140.5961 | 40.1443 | 0 | 0
2014-07-12 | 0 | 0 | 0.45 | 51.11 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 140.9046 | 40.4528 | 0 | 0
2014-07-13 | 0 | 0 | 0.45 | 50.66 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 141.2132 | 40.7614 | 0 | 0
2014-07-14 | 0 | 0 | 0.45 | 50.21 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 141.5218 | 41.07 | 0 | 0
2014-07-15 | 0 | 0 | 0.45 | 49.76 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 141.8303 | 41.3785 | 0 | 0
2014-07-16 | 0 | 0 | 0.45 | 49.31 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 142.1389 | 41.6871 | 0 | 0
2014-07-17 | 0 | 0 | 0.45 | 48.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 142.4475 | 41.9957 | 0 | 0
2014-07-18 | 37 | 2.5 | 0.45 | 50.91 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 144.5889 | 44.1371 | 0 | 0
2014-07-19 | 1.8 | 0.18 | 0.45 | 50.64 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 145.0294 | 44.5776 | 0 | 0
2014-07-20 | 0 | 0 | 0.45 | 50.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 145.338 | 44.8862 | 0 | 0
2014-07-21 | 0 | 0 | 0.45 | 49.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 145.6466 | 45.1948 | 0 | 0
2014-07-22 | 8 | 0.8 | 0.45 | 50.09 | 190000 | 211111.1111 | 0.21111 | 4000 | 4 | 8000000 | 8 | 1200 | 4.32 | 12.5311 | 0.89508 | 146.5417 | 46.0899 | 0 | 0
2014-07-23 | 18.2 | 1.82 | 0.45 | 51.46 | 190000 | 480277.7778 | 0.48028 | 9100 | 9.1 | 18200000 | 18.2 | 1200 | 4.32 | 23.0003 | 1.6429 | 148.1845 | 47.7327 | 0 | 0
2014-07-24 | 0.6 | 0.06 | 0.45 | 51.07 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 148.5371 | 48.0853 | 0 | 0
2014-07-25 | 0 | 0 | 0.45 | 50.62 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 148.8457 | 48.3939 | 0 | 0
2014-07-26 | 0 | 0 | 0.45 | 50.17 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 149.1542 | 48.7024 | 0 | 0
2014-07-27 | 0 | 0 | 0.45 | 49.72 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 149.4628 | 49.011 | 0 | 0
2014-07-28 | 0 | 0 | 0.45 | 49.27 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 149.7714 | 49.3196 | 0 | 0
2014-07-29 | 0 | 0 | 0.45 | 48.82 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 150.08 | 49.6281 | 0 | 0
2014-07-30 | 0 | 0 | 0.45 | 48.37 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 150.3885 | 49.9367 | 0 | 0
2014-07-31 | 0 | 0 | 0.45 | 47.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 150.6971 | 50.2453 | 0 | 0
2014-08-01 | 0 | 0 | 0.45 | 47.47 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.0057 | 50.5539 | 0 | 0
2014-08-02 | 0 | 0 | 0.45 | 47.02 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.3142 | 50.8624 | 0 | 0
2014-08-03 | 0 | 0 | 0.45 | 46.57 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.6228 | 51.171 | 0 | 0
2014-08-04 | 0 | 0 | 0.45 | 46.12 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.9314 | 51.4796 | 0 | 0
2014-08-05 | 0 | 0 | 0.45 | 45.67 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 152.24 | 51.7881 | 0 | 0
2014-08-06 | 0 | 0 | 0.45 | 45.22 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 152.5485 | 52.0967 | 0 | 0
2014-08-07 | 0 | 0 | 0.45 | 44.77 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 152.8571 | 52.4053 | 0 | 0
2014-08-08 | 0 | 0 | 0.45 | 44.32 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.1657 | 52.7139 | 0 | 0
2014-08-09 | 0 | 0 | 0.45 | 43.87 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.4742 | 53.0224 | 0 | 0
2014-08-10 | 0 | 0 | 0.45 | 43.42 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.7828 | 53.331 | 0 | 0
2014-08-11 | 0 | 0 | 0.45 | 42.97 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 154.0914 | 53.6396 | 0 | 0
2014-08-12 | 0 | 0 | 0.45 | 42.52 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 154.4 | 53.9481 | 0 | 0
2014-08-13 | 0 | 0 | 0.45 | 42.07 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 154.7085 | 54.2567 | 0 | 0
2014-08-14 | 0 | 0 | 0.45 | 41.62 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 155.0171 | 54.5653 | 0 | 0
2014-08-15 | 0 | 0 | 0.45 | 41.17 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 155.3257 | 54.8739 | 0 | 0
2014-08-16 | 0 | 0 | 0.45 | 40.72 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 155.6342 | 55.1824 | 0 | 0
2014-08-17 | 0 | 0 | 0.45 | 40.27 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 155.9428 | 55.491 | 0 | 0
2014-08-18 | 0 | 0 | 0.45 | 39.82 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 156.2514 | 55.7996 | 0 | 0
2014-08-19 | 0 | 0 | 0.45 | 39.37 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 156.56 | 56.1081 | 0 | 0
2014-08-20 | 0 | 0 | 0.45 | 38.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 156.8685 | 56.4167 | 0 | 0
2014-08-21 | 0 | 0 | 0.45 | 38.47 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 157.1771 | 56.7253 | 0 | 0
2014-08-22 | 0 | 0 | 0.45 | 38.02 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 157.4857 | 57.0339 | 0 | 0
2014-08-23 | 0 | 0 | 0.45 | 37.57 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 157.7942 | 57.3424 | 0 | 0
2014-08-24 | 0 | 0 | 0.45 | 37.12 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 158.1028 | 57.651 | 0 | 0
2014-08-25 | 0 | 0 | 0.45 | 36.67 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 158.4114 | 57.9596 | 0 | 0
2014-08-26 | 0 | 0 | 0.45 | 36.22 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 158.72 | 58.2681 | 0 | 0
2014-08-27 | 0 | 0 | 0.45 | 35.77 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 159.0285 | 58.5767 | 0 | 0
2014-08-28 | 0.4 | 0.04 | 0.45 | 35.36 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 159.3664 | 58.9146 | 0 | 0
2014-08-29 | 7.8 | 0.78 | 0.45 | 35.69 | 190000 | 205833.3333 | 0.20583 | 3900 | 3.9 | 7800000 | 7.8 | 1200 | 4.32 | 12.3258 | 0.88042 | 160.2468 | 59.795 | 0 | 0
2014-08-30 | 3.6 | 0.36 | 0.45 | 35.6 | 190000 | 95000 | 0.095 | 1800 | 1.8 | 3600000 | 3.6 | 1200 | 4.32 | 8.015 | 0.5725 | 160.8193 | 60.3675 | 0 | 0
2014-08-31 | 10.6 | 1.06 | 0.45 | 36.21 | 190000 | 279722.2222 | 0.27972 | 5300 | 5.3 | 10600000 | 10.6 | 1200 | 4.32 | 15.1997 | 1.0857 | 161.905 | 61.4532 | 0 | 0
2014-09-01 | 3.2 | 0.32 | 0.45 | 36.08 | 190000 | 84444.4444 | 0.084444 | 1600 | 1.6 | 3200000 | 3.2 | 1200 | 4.32 | 7.6044 | 0.54317 | 162.4482 | 61.9964 | 0 | 0
2014-09-02 | 6.2 | 0.62 | 0.45 | 36.25 | 190000 | 163611.1111 | 0.16361 | 3100 | 3.1 | 6200000 | 6.2 | 1200 | 4.32 | 10.6836 | 0.76312 | 163.2113 | 62.7595 | 0 | 0
2014-09-03 | 0 | 0 | 0.45 | 35.8 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 163.5199 | 63.0681 | 0 | 0
2014-09-04 | 0 | 0 | 0.45 | 35.35 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 163.8285 | 63.3767 | 0 | 0
2014-09-05 | 0 | 0 | 0.45 | 34.9 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 164.137 | 63.6852 | 0 | 0
2014-09-06 | 0 | 0 | 0.45 | 34.45 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 164.4456 | 63.9938 | 0 | 0
2014-09-07 | 0 | 0 | 0.45 | 34 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 164.7542 | 64.3024 | 0 | 0
2014-09-08 | 0 | 0 | 0.45 | 33.55 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.0627 | 64.6109 | 0 | 0
2014-09-09 | 0 | 0 | 0.45 | 33.1 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.3713 | 64.9195 | 0 | 0
2014-09-10 | 0 | 0 | 0.45 | 32.65 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.6799 | 65.2281 | 0 | 0
2014-09-11 | 0 | 0 | 0.45 | 32.2 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.9885 | 65.5367 | 0 | 0
2014-09-12 | 0 | 0 | 0.45 | 31.75 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 166.297 | 65.8452 | 0 | 0
2014-09-13 | 0 | 0 | 0.45 | 31.3 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 166.6056 | 66.1538 | 0 | 0
2014-09-14 | 0 | 0 | 0.45 | 30.85 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 166.9142 | 66.4624 | 0 | 0
2014-09-15 | 0 | 0 | 0.45 | 30.4 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 167.2227 | 66.7709 | 0 | 0
2014-09-16 | 0 | 0 | 0.45 | 29.95 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 167.5313 | 67.0795 | 0 | 0
2014-09-17 | 0 | 0 | 0.45 | 29.5 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 167.8399 | 67.3881 | 0 | 0
2014-09-18 | 26.4 | 2.5 | 0.45 | 31.55 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 169.9813 | 69.5295 | 0 | 0
2014-09-19 | 0.4 | 0.04 | 0.45 | 31.14 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 170.3192 | 69.8674 | 0 | 0
2014-09-20 | 0 | 0 | 0.45 | 30.69 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 170.6278 | 70.176 | 0 | 0
2014-09-21 | 2 | 0.2 | 0.45 | 30.44 | 190000 | 52777.7778 | 0.052778 | 1000 | 1 | 2000000 | 2 | 1200 | 4.32 | 6.3728 | 0.4552 | 171.083 | 70.6312 | 0 | 0
2014-09-22 | 12.4 | 1.24 | 0.45 | 31.23 | 190000 | 327222.2222 | 0.32722 | 6200 | 6.2 | 12400000 | 12.4 | 1200 | 4.32 | 17.0472 | 1.2177 | 172.3006 | 71.8488 | 0 | 0
2014-09-23 | 29.4 | 2.5 | 0.45 | 33.28 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 174.442 | 73.9902 | 0 | 0
2014-09-24 | 1.6 | 0.16 | 0.45 | 32.99 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 174.8679 | 74.4161 | 0 | 0
2014-09-25 | 0.6 | 0.06 | 0.45 | 32.6 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 175.2205 | 74.7687 | 0 | 0
2014-09-26 | 8.2 | 0.82 | 0.45 | 32.97 | 190000 | 216388.8889 | 0.21639 | 4100 | 4.1 | 8200000 | 8.2 | 1200 | 4.32 | 12.7364 | 0.90974 | 176.1302 | 75.6784 | 0 | 0
2014-09-27 | 0 | 0 | 0.45 | 32.52 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 176.4388 | 75.987 | 0 | 0
2014-09-28 | 12.4 | 1.24 | 0.45 | 33.31 | 190000 | 327222.2222 | 0.32722 | 6200 | 6.2 | 12400000 | 12.4 | 1200 | 4.32 | 17.0472 | 1.2177 | 177.6564 | 77.2046 | 0 | 0
2014-09-29 | 5.6 | 0.56 | 0.45 | 33.42 | 190000 | 147777.7778 | 0.14778 | 2800 | 2.8 | 5600000 | 5.6 | 1200 | 4.32 | 10.0678 | 0.71913 | 178.3756 | 77.9238 | 0 | 0
2014-09-30 | 0 | 0 | 0.45 | 32.97 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 178.6841 | 78.2323 | 0 | 0
2014-10-01 | 0 | 0 | 0.45 | 32.52 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 178.9927 | 78.5409 | 0 | 0
2014-10-02 | 0 | 0 | 0.45 | 32.07 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 179.3013 | 78.8495 | 0 | 0
2014-10-03 | 57.8 | 2.5 | 0.45 | 34.12 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 181.4427 | 80.9909 | 0 | 0
2014-10-04 | 6 | 0.6 | 0.45 | 34.27 | 190000 | 158333.3333 | 0.15833 | 3000 | 3 | 6000000 | 6 | 1200 | 4.32 | 10.4783 | 0.74845 | 182.1911 | 81.7393 | 0 | 0
2014-10-05 | 9.2 | 0.92 | 0.45 | 34.74 | 190000 | 242777.7778 | 0.24278 | 4600 | 4.6 | 9200000 | 9.2 | 1200 | 4.32 | 13.7628 | 0.98306 | 183.1742 | 82.7224 | 0 | 0
2014-10-06 | 0.4 | 0.04 | 0.45 | 34.33 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 183.5121 | 83.0603 | 0 | 0
2014-10-07 | 0 | 0 | 0.45 | 33.88 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 183.8207 | 83.3689 | 0 | 0
2014-10-08 | 1.4 | 0.14 | 0.45 | 33.57 | 190000 | 36944.4444 | 0.036944 | 700 | 0.7 | 1400000 | 1.4 | 1200 | 4.32 | 5.7569 | 0.41121 | 184.2319 | 83.7801 | 0 | 0
2014-10-09 | 1.8 | 0.18 | 0.45 | 33.3 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 184.6724 | 84.2206 | 0 | 0
2014-10-10 | 17.8 | 1.78 | 0.45 | 34.63 | 190000 | 469722.2222 | 0.46972 | 8900 | 8.9 | 17800000 | 17.8 | 1200 | 4.32 | 22.5897 | 1.6136 | 186.286 | 85.8342 | 0 | 0
2014-10-11 | 15.4 | 1.54 | 0.45 | 35.72 | 190000 | 406388.8889 | 0.40639 | 7700 | 7.7 | 15400000 | 15.4 | 1200 | 4.32 | 20.1264 | 1.4376 | 187.7236 | 87.2718 | 0 | 0
2014-10-12 | 33 | 2.5 | 0.45 | 37.77 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 189.865 | 89.4132 | 0 | 0
2014-10-13 | 31.4 | 2.5 | 0.45 | 39.82 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 192.0064 | 91.5546 | 0 | 0
2014-10-14 | 28.4 | 2.5 | 0.45 | 41.87 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 194.1478 | 93.696 | 0 | 0
2014-10-15 | 6.4 | 0.64 | 0.45 | 42.06 | 190000 | 168888.8889 | 0.16889 | 3200 | 3.2 | 6400000 | 6.4 | 1200 | 4.32 | 10.8889 | 0.77778 | 194.9256 | 94.4738 | 0 | 0
2014-10-16 | 17.2 | 1.72 | 0.45 | 43.33 | 190000 | 453888.8889 | 0.45389 | 8600 | 8.6 | 17200000 | 17.2 | 1200 | 4.32 | 21.9739 | 1.5696 | 196.4951 | 96.0433 | 0 | 0
2014-10-17 | 27 | 2.5 | 0.45 | 45.38 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 198.6365 | 98.1847 | 0 | 0
2014-10-18 | 16.8 | 1.68 | 0.45 | 46.61 | 190000 | 443333.3333 | 0.44333 | 8400 | 8.4 | 16800000 | 16.8 | 1200 | 4.32 | 21.5633 | 1.5402 | 200.1768 | 99.725 | 0 | 0
2014-10-19 | 46.2 | 2.5 | 0.45 | 48.66 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 202.3182 | 0 | 0 | 1
2014-10-20 | 10.8 | 1.08 | 0.45 | 49.29 | 190000 | 285000 | 0.285 | 5400 | 5.4 | 10800000 | 10.8 | 1200 | 4.32 | 15.405 | 1.1004 | 203.4185 | 1.1004 | 0 | 0
2014-10-21 | 40.2 | 2.5 | 0.45 | 51.34 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 205.56 | 3.2418 | 0 | 0
2014-10-22 | 21.4 | 2.14 | 0.45 | 53.03 | 190000 | 564722.2222 | 0.56472 | 10700 | 10.7 | 21400000 | 21.4 | 1200 | 4.32 | 26.2847 | 1.8775 | 207.4374 | 5.1192 | 0 | 0
2014-10-23 | 9.4 | 0.94 | 0.45 | 53.52 | 190000 | 248055.5556 | 0.24806 | 4700 | 4.7 | 9400000 | 9.4 | 1200 | 4.32 | 13.9681 | 0.99772 | 208.4351 | 6.117 | 0 | 0
2014-10-24 | 1.6 | 0.16 | 0.45 | 53.23 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 208.861 | 6.5428 | 0 | 0
2014-10-25 | 21.8 | 2.18 | 0.45 | 54.96 | 190000 | 575277.7778 | 0.57528 | 10900 | 10.9 | 21800000 | 21.8 | 1200 | 4.32 | 26.6953 | 1.9068 | 210.7678 | 8.4496 | 0 | 0
2014-10-26 | 2.4 | 0.24 | 0.45 | 54.75 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 211.2524 | 8.9342 | 0 | 0
2014-10-27 | 33.6 | 2.5 | 0.45 | 56.8 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 213.3938 | 11.0756 | 0 | 0
2014-10-28 | 24.4 | 2.44 | 0.45 | 58.79 | 190000 | 643888.8889 | 0.64389 | 12200 | 12.2 | 24400000 | 24.4 | 1200 | 4.32 | 29.3639 | 2.0974 | 215.4912 | 13.173 | 0 | 0
2014-10-29 | 7 | 0.7 | 0.45 | 59.04 | 190000 | 184722.2222 | 0.18472 | 3500 | 3.5 | 7000000 | 7 | 1200 | 4.32 | 11.5047 | 0.82177 | 216.3129 | 13.9948 | 0 | 0
2014-10-30 | 9 | 0.9 | 0.45 | 59.49 | 190000 | 237500 | 0.2375 | 4500 | 4.5 | 9000000 | 9 | 1200 | 4.32 | 13.5575 | 0.96839 | 217.2813 | 14.9632 | 0 | 0
2014-10-31 | 15 | 1.5 | 0.45 | 60.54 | 190000 | 395833.3333 | 0.39583 | 7500 | 7.5 | 15000000 | 15 | 1200 | 4.32 | 19.7158 | 1.4083 | 218.6896 | 16.3714 | 0 | 0
2014-11-01 | 6.4 | 0.64 | 0.45 | 60.73 | 190000 | 168888.8889 | 0.16889 | 3200 | 3.2 | 6400000 | 6.4 | 1200 | 4.32 | 10.8889 | 0.77778 | 219.4674 | 17.1492 | 0 | 0
2014-11-02 | 37.6 | 2.5 | 0.45 | 62.78 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 221.6088 | 19.2906 | 0 | 0
2014-11-03 | 35.2 | 2.5 | 0.45 | 64.83 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 223.7502 | 21.432 | 0 | 0
2014-11-04 | 9 | 0.9 | 0.45 | 65.28 | 190000 | 237500 | 0.2375 | 4500 | 4.5 | 9000000 | 9 | 1200 | 4.32 | 13.5575 | 0.96839 | 224.7186 | 22.4004 | 0 | 0
2014-11-05 | 4.4 | 0.44 | 0.45 | 65.27 | 190000 | 116111.1111 | 0.11611 | 2200 | 2.2 | 4400000 | 4.4 | 1200 | 4.32 | 8.8361 | 0.63115 | 225.3498 | 23.0316 | 0 | 0
2014-11-06 | 20.2 | 2.02 | 0.45 | 66.84 | 190000 | 533055.5556 | 0.53306 | 10100 | 10.1 | 20200000 | 20.2 | 1200 | 4.32 | 25.0531 | 1.7895 | 227.1393 | 24.8211 | 0 | 0
2014-11-07 | 1.4 | 0.14 | 0.45 | 66.53 | 190000 | 36944.4444 | 0.036944 | 700 | 0.7 | 1400000 | 1.4 | 1200 | 4.32 | 5.7569 | 0.41121 | 227.5505 | 25.2323 | 0 | 0
2014-11-08 | 34 | 2.5 | 0.45 | 68.58 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 229.6919 | 27.3737 | 0 | 0
2014-11-09 | 0 | 0 | 0.45 | 68.13 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 230.0004 | 27.6823 | 0 | 0
2014-11-10 | 0 | 0 | 0.45 | 67.68 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 230.309 | 27.9908 | 0 | 0
2014-11-11 | 0 | 0 | 0.45 | 67.23 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 230.6176 | 28.2994 | 0 | 0
2014-11-12 | 0 | 0 | 0.45 | 66.78 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 230.9262 | 28.608 | 0 | 0
2014-11-13 | 0 | 0 | 0.45 | 66.33 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 231.2347 | 28.9165 | 0 | 0
2014-11-14 | 0 | 0 | 0.45 | 65.88 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 231.5433 | 29.2251 | 0 | 0
2014-11-15 | 0 | 0 | 0.45 | 65.43 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 231.8519 | 29.5337 | 0 | 0
2014-11-16 | 0 | 0 | 0.45 | 64.98 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 232.1604 | 29.8423 | 0 | 0
2014-11-17 | 0 | 0 | 0.45 | 64.53 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 232.469 | 30.1508 | 0 | 0
2014-11-18 | 0 | 0 | 0.45 | 64.08 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 232.7776 | 30.4594 | 0 | 0
2014-11-19 | 3.4 | 0.34 | 0.45 | 63.97 | 190000 | 89722.2222 | 0.089722 | 1700 | 1.7 | 3400000 | 3.4 | 1200 | 4.32 | 7.8097 | 0.55784 | 233.3354 | 31.0172 | 0 | 0
2014-11-20 | 29.4 | 2.5 | 0.45 | 66.02 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 235.4768 | 33.1587 | 0 | 0
2014-11-21 | 32.8 | 2.5 | 0.45 | 68.07 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 237.6182 | 35.3001 | 0 | 0
2014-11-22 | 25.6 | 2.5 | 0.45 | 70.12 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 239.7597 | 37.4415 | 0 | 0
2014-11-23 | 15.2 | 1.52 | 0.45 | 71.19 | 190000 | 401111.1111 | 0.40111 | 7600 | 7.6 | 15200000 | 15.2 | 1200 | 4.32 | 19.9211 | 1.4229 | 241.1826 | 38.8644 | 0 | 0
2014-11-24 | 60.6 | 2.5 | 0.45 | 73.24 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 243.324 | 41.0058 | 0 | 0
2014-11-25 | 15 | 1.5 | 0.45 | 74.29 | 190000 | 395833.3333 | 0.39583 | 7500 | 7.5 | 15000000 | 15 | 1200 | 4.32 | 19.7158 | 1.4083 | 244.7323 | 42.4141 | 0 | 0
2014-11-26 | 43 | 2.5 | 0.45 | 76.34 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 246.8737 | 44.5555 | 0 | 0
2014-11-27 | 15 | 1.5 | 0.45 | 77.39 | 190000 | 395833.3333 | 0.39583 | 7500 | 7.5 | 15000000 | 15 | 1200 | 4.32 | 19.7158 | 1.4083 | 248.282 | 45.9638 | 0 | 0
2014-11-28 | 0 | 0 | 0.45 | 76.94 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 248.5905 | 46.2723 | 0 | 0
2014-11-29 | 0 | 0 | 0.45 | 76.49 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 248.8991 | 46.5809 | 0 | 0
2014-11-30 | 0 | 0 | 0.45 | 76.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 249.2077 | 46.8895 | 0 | 0
2014-12-01 | 0 | 0 | 0.45 | 75.59 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 249.5162 | 47.1981 | 0 | 0
2014-12-02 | 0 | 0 | 0.45 | 75.14 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 249.8248 | 47.5066 | 0 | 0
2014-12-03 | 0 | 0 | 0.45 | 74.69 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 0 | 47.8152 | 1 | 0
2014-12-04 | 1.2 | 0.12 | 0.45 | 74.36 | 190000 | 31666.6667 | 0.031667 | 600 | 0.6 | 1200000 | 1.2 | 1200 | 4.32 | 5.5517 | 0.39655 | 0.39655 | 48.2117 | 0 | 0
2014-12-05 | 45.4 | 2.5 | 0.45 | 76.41 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 2.538 | 50.3532 | 0 | 0
2014-12-06 | 0.8 | 0.08 | 0.45 | 76.04 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 2.9052 | 50.7204 | 0 | 0
2014-12-07 | 15.2 | 1.52 | 0.45 | 77.11 | 190000 | 401111.1111 | 0.40111 | 7600 | 7.6 | 15200000 | 15.2 | 1200 | 4.32 | 19.9211 | 1.4229 | 4.3281 | 52.1433 | 0 | 0
2014-12-08 | 48.6 | 2.5 | 0.45 | 79.16 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 6.4695 | 54.2847 | 0 | 0
2014-12-09 | 34.2 | 2.5 | 0.45 | 81.21 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 8.6109 | 56.4261 | 0 | 0
2014-12-10 | 4.4 | 0.44 | 0.45 | 81.2 | 190000 | 116111.1111 | 0.11611 | 2200 | 2.2 | 4400000 | 4.4 | 1200 | 4.32 | 8.8361 | 0.63115 | 9.2421 | 57.0573 | 0 | 0
2014-12-11 | 17.8 | 1.78 | 0.45 | 82.53 | 190000 | 469722.2222 | 0.46972 | 8900 | 8.9 | 17800000 | 17.8 | 1200 | 4.32 | 22.5897 | 1.6136 | 10.8556 | 58.6708 | 0 | 0
2014-12-12 | 1.4 | 0.14 | 0.45 | 82.22 | 190000 | 36944.4444 | 0.036944 | 700 | 0.7 | 1400000 | 1.4 | 1200 | 4.32 | 5.7569 | 0.41121 | 11.2668 | 59.082 | 0 | 0
2014-12-13 | 1 | 0.1 | 0.45 | 81.87 | 190000 | 26388.8889 | 0.026389 | 500 | 0.5 | 1000000 | 1 | 1200 | 4.32 | 5.3464 | 0.38188 | 11.6487 | 59.4639 | 0 | 0
2014-12-14 | 0 | 0 | 0.45 | 81.42 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 11.9573 | 59.7725 | 0 | 0
2014-12-15 | 9 | 0.9 | 0.45 | 81.87 | 190000 | 237500 | 0.2375 | 4500 | 4.5 | 9000000 | 9 | 1200 | 4.32 | 13.5575 | 0.96839 | 12.9257 | 60.7409 | 0 | 0
2014-12-16 | 20.2 | 2.02 | 0.45 | 83.44 | 190000 | 533055.5556 | 0.53306 | 10100 | 10.1 | 20200000 | 20.2 | 1200 | 4.32 | 25.0531 | 1.7895 | 14.7152 | 62.5304 | 0 | 0
2014-12-17 | 0.8 | 0.08 | 0.45 | 83.07 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 15.0824 | 62.8976 | 0 | 0
2014-12-18 | 24.6 | 2.46 | 0.45 | 85.08 | 190000 | 649166.6667 | 0.64917 | 12300 | 12.3 | 24600000 | 24.6 | 1200 | 4.32 | 29.5692 | 2.1121 | 17.1945 | 65.0097 | 0 | 0
2014-12-19 | 0 | 0 | 0.45 | 84.63 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 17.5031 | 65.3183 | 0 | 0
2014-12-20 | 0 | 0 | 0.45 | 84.18 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 17.8116 | 65.6268 | 0 | 0
2014-12-21 | 8.8 | 0.88 | 0.45 | 84.61 | 190000 | 232222.2222 | 0.23222 | 4400 | 4.4 | 8800000 | 8.8 | 1200 | 4.32 | 13.3522 | 0.95373 | 18.7654 | 66.5806 | 0 | 0
2014-12-22 | 11.6 | 1.16 | 0.45 | 85.32 | 190000 | 306111.1111 | 0.30611 | 5800 | 5.8 | 11600000 | 11.6 | 1200 | 4.32 | 16.2261 | 1.159 | 19.9244 | 67.7396 | 0 | 0
2014-12-23 | 10 | 1 | 0.45 | 85.87 | 190000 | 263888.8889 | 0.26389 | 5000 | 5 | 10000000 | 10 | 1200 | 4.32 | 14.5839 | 1.0417 | 20.9661 | 68.7813 | 0 | 0
2014-12-24 | 2.2 | 0.22 | 0.45 | 85.64 | 190000 | 58055.5556 | 0.058056 | 1100 | 1.1 | 2200000 | 2.2 | 1200 | 4.32 | 6.5781 | 0.46986 | 21.436 | 69.2512 | 0 | 0
2014-12-25 | 0.6 | 0.06 | 0.45 | 85.25 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 21.7885 | 69.6037 | 0 | 0
2014-12-26 | 10.2 | 1.02 | 0.45 | 85.82 | 190000 | 269166.6667 | 0.26917 | 5100 | 5.1 | 10200000 | 10.2 | 1200 | 4.32 | 14.7892 | 1.0564 | 22.8449 | 70.6601 | 0 | 0
2014-12-27 | 5.4 | 0.54 | 0.45 | 85.91 | 190000 | 142500 | 0.1425 | 2700 | 2.7 | 5400000 | 5.4 | 1200 | 4.32 | 9.8625 | 0.70446 | 23.5493 | 71.3645 | 0 | 0
2014-12-28 | 0 | 0 | 0.45 | 85.46 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 23.8579 | 71.6731 | 0 | 0
2014-12-29 | 0 | 0 | 0.45 | 85.01 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 24.1665 | 71.9817 | 0 | 0
2014-12-30 | 0 | 0 | 0.45 | 84.56 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 24.4751 | 72.2903 | 0 | 0
2014-12-31 | 0 | 0 | 0.45 | 84.11 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 24.7836 | 72.5988 | 0 | 0
2015-01-01 | 7.8 | 0.78 | 0.45 | 84.44 | 190000 | 205833.3333 | 0.20583 | 3900 | 3.9 | 7800000 | 7.8 | 1200 | 4.32 | 12.3258 | 0.88042 | 25.664 | 73.4792 | 0 | 0
2015-01-02 | 1 | 0.1 | 0.45 | 84.09 | 190000 | 26388.8889 | 0.026389 | 500 | 0.5 | 1000000 | 1 | 1200 | 4.32 | 5.3464 | 0.38188 | 26.0459 | 73.8611 | 0 | 0
2015-01-03 | 13.4 | 1.34 | 0.45 | 84.98 | 190000 | 353611.1111 | 0.35361 | 6700 | 6.7 | 13400000 | 13.4 | 1200 | 4.32 | 18.0736 | 1.291 | 27.3369 | 75.1521 | 0 | 0
2015-01-04 | 64.2 | 2.5 | 0.45 | 87.03 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 29.4783 | 77.2935 | 0 | 0
2015-01-05 | 32.2 | 2.5 | 0.45 | 89.08 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 31.6197 | 79.4349 | 0 | 0
2015-01-06 | 2.8 | 0.28 | 0.45 | 88.91 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 32.1336 | 79.9488 | 0 | 0
2015-01-07 | 0 | 0 | 0.45 | 88.46 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 32.4421 | 80.2573 | 0 | 0
2015-01-08 | 0 | 0 | 0.45 | 88.01 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 32.7507 | 80.5659 | 0 | 0
2015-01-09 | 0.8 | 0.08 | 0.45 | 87.64 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 33.1179 | 80.9331 | 0 | 0
2015-01-10 | 0 | 0 | 0.45 | 87.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 33.4265 | 81.2417 | 0 | 0
2015-01-11 | 0 | 0 | 0.45 | 86.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 33.7351 | 81.5503 | 0 | 0
2015-01-12 | 0 | 0 | 0.45 | 86.29 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 34.0437 | 81.8588 | 0 | 0
2015-01-13 | 0 | 0 | 0.45 | 85.84 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 34.3522 | 82.1674 | 0 | 0
2015-01-14 | 0.4 | 0.04 | 0.45 | 85.43 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 34.6901 | 82.5053 | 0 | 0
2015-01-15 | 35.4 | 2.5 | 0.45 | 87.48 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 36.8315 | 84.6467 | 0 | 0
2015-01-16 | 6 | 0.6 | 0.45 | 87.63 | 190000 | 158333.3333 | 0.15833 | 3000 | 3 | 6000000 | 6 | 1200 | 4.32 | 10.4783 | 0.74845 | 37.58 | 85.3952 | 0 | 0
2015-01-17 | 20.4 | 2.04 | 0.45 | 89.22 | 190000 | 538333.3333 | 0.53833 | 10200 | 10.2 | 20400000 | 20.4 | 1200 | 4.32 | 25.2583 | 1.8042 | 39.3841 | 87.1993 | 0 | 0
2015-01-18 | 16.6 | 1.66 | 0.45 | 90.43 | 190000 | 438055.5556 | 0.43806 | 8300 | 8.3 | 16600000 | 16.6 | 1200 | 4.32 | 21.3581 | 1.5256 | 40.9097 | 88.7249 | 0 | 0
2015-01-19 | 2.6 | 0.26 | 0.45 | 90.24 | 190000 | 68611.1111 | 0.068611 | 1300 | 1.3 | 2600000 | 2.6 | 1200 | 4.32 | 6.9886 | 0.49919 | 41.4089 | 89.2241 | 0 | 0
2015-01-20 | 0.4 | 0.04 | 0.45 | 89.83 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 41.7468 | 89.562 | 0 | 0
2015-01-21 | 18.4 | 1.84 | 0.45 | 91.22 | 190000 | 485555.5556 | 0.48556 | 9200 | 9.2 | 18400000 | 18.4 | 1200 | 4.32 | 23.2056 | 1.6575 | 43.4043 | 91.2195 | 0 | 0
2015-01-22 | 14 | 1.4 | 0.45 | 92.17 | 190000 | 369444.4444 | 0.36944 | 7000 | 7 | 14000000 | 14 | 1200 | 4.32 | 18.6894 | 1.335 | 44.7393 | 92.5545 | 0 | 0
2015-01-23 | 90.8 | 2.5 | 0.45 | 94.22 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 46.8807 | 94.6959 | 0 | 0
2015-01-24 | 40 | 2.5 | 0.45 | 96.27 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 49.0221 | 96.8373 | 0 | 0
2015-01-25 | 1.8 | 0.18 | 0.45 | 96 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 49.4627 | 97.2779 | 0 | 0
2015-01-26 | 2.8 | 0.28 | 0.45 | 95.83 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 49.9765 | 97.7917 | 0 | 0
2015-01-27 | 2.8 | 0.28 | 0.45 | 95.66 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 50.4904 | 98.3056 | 0 | 0
2015-01-28 | 0 | 0 | 0.45 | 95.21 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 50.7989 | 98.6141 | 0 | 0
2015-01-29 | 0 | 0 | 0.45 | 94.76 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 51.1075 | 98.9227 | 0 | 0
2015-01-30 | 0.6 | 0.06 | 0.45 | 94.37 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 51.4601 | 99.2753 | 0 | 0
2015-01-31 | 5.8 | 0.58 | 0.45 | 94.5 | 190000 | 153055.5556 | 0.15306 | 2900 | 2.9 | 5800000 | 5.8 | 1200 | 4.32 | 10.2731 | 0.73379 | 52.1938 | 0 | 0 | 1
2015-02-01 | 8 | 0.8 | 0.45 | 94.85 | 190000 | 211111.1111 | 0.21111 | 4000 | 4 | 8000000 | 8 | 1200 | 4.32 | 12.5311 | 0.89508 | 53.0889 | 0.89508 | 0 | 0
2015-02-02 | 27 | 2.5 | 0.45 | 96.9 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 55.2303 | 3.0365 | 0 | 0
2015-02-03 | 0.6 | 0.06 | 0.45 | 96.51 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 55.5829 | 3.389 | 0 | 0
2015-02-04 | 36 | 2.5 | 0.45 | 98.56 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 57.7243 | 5.5305 | 0 | 0
2015-02-05 | 27.2 | 2.5 | 0.45 | 100.61 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 59.8657 | 7.6719 | 0 | 0
2015-02-06 | 28.2 | 2.5 | 0.45 | 102.66 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 62.0071 | 9.8133 | 0 | 0
2015-02-07 | 39.2 | 2.5 | 0.45 | 104.71 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 64.1485 | 11.9547 | 0 | 0
2015-02-08 | 6.6 | 0.66 | 0.45 | 104.92 | 190000 | 174166.6667 | 0.17417 | 3300 | 3.3 | 6600000 | 6.6 | 1200 | 4.32 | 11.0942 | 0.79244 | 64.941 | 12.7471 | 0 | 0
2015-02-09 | 3.2 | 0.32 | 0.45 | 104.79 | 190000 | 84444.4444 | 0.084444 | 1600 | 1.6 | 3200000 | 3.2 | 1200 | 4.32 | 7.6044 | 0.54317 | 65.4841 | 13.2903 | 0 | 0
2015-02-10 | 0.2 | 0.02 | 0.45 | 104.36 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 65.8074 | 13.6135 | 0 | 0
2015-02-11 | 19.6 | 1.96 | 0.45 | 105.87 | 190000 | 517222.2222 | 0.51722 | 9800 | 9.8 | 19600000 | 19.6 | 1200 | 4.32 | 24.4372 | 1.7455 | 67.5529 | 15.359 | 0 | 0
2015-02-12 | 30.4 | 2.5 | 0.45 | 107.92 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 69.6943 | 17.5005 | 0 | 0
2015-02-13 | 19 | 1.9 | 0.45 | 109.37 | 190000 | 501388.8889 | 0.50139 | 9500 | 9.5 | 19000000 | 19 | 1200 | 4.32 | 23.8214 | 1.7015 | 71.3958 | 19.202 | 0 | 0
2015-02-14 | 0.2 | 0.02 | 0.45 | 108.94 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 71.7191 | 19.5252 | 0 | 0
2015-02-15 | 0 | 0 | 0.45 | 108.49 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 72.0276 | 19.8338 | 0 | 0
2015-02-16 | 0 | 0 | 0.45 | 108.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 72.3362 | 20.1424 | 0 | 0
2015-02-17 | 0 | 0 | 0.45 | 107.59 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 72.6448 | 20.4509 | 0 | 0
2015-02-18 | 4 | 0.4 | 0.45 | 107.54 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 73.2466 | 21.0528 | 0 | 0
2015-02-19 | 11 | 1.1 | 0.45 | 108.19 | 190000 | 290277.7778 | 0.29028 | 5500 | 5.5 | 11000000 | 11 | 1200 | 4.32 | 15.6103 | 1.115 | 74.3616 | 22.1678 | 0 | 0
2015-02-20 | 0.4 | 0.04 | 0.45 | 107.78 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 74.6995 | 22.5057 | 0 | 0
2015-02-21 | 0 | 0 | 0.45 | 107.33 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 75.0081 | 22.8142 | 0 | 0
2015-02-22 | 0 | 0 | 0.45 | 106.88 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 75.3167 | 23.1228 | 0 | 0
2015-02-23 | 0 | 0 | 0.45 | 106.43 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 75.6252 | 23.4314 | 0 | 0
2015-02-24 | 0.2 | 0.02 | 0.45 | 106 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 75.9485 | 23.7546 | 0 | 0
2015-02-25 | 4.6 | 0.46 | 0.45 | 106.01 | 190000 | 121388.8889 | 0.12139 | 2300 | 2.3 | 4600000 | 4.6 | 1200 | 4.32 | 9.0414 | 0.64581 | 76.5943 | 24.4004 | 0 | 0
2015-02-26 | 8.8 | 0.88 | 0.45 | 106.44 | 190000 | 232222.2222 | 0.23222 | 4400 | 4.4 | 8800000 | 8.8 | 1200 | 4.32 | 13.3522 | 0.95373 | 77.548 | 25.3542 | 0 | 0
2015-02-27 | 0.4 | 0.04 | 0.45 | 106.03 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 77.8859 | 25.6921 | 0 | 0
2015-02-28 | 0 | 0 | 0.45 | 105.58 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 78.1945 | 26.0006 | 0 | 0
2015-03-01 | 1.2 | 0.12 | 0.45 | 105.25 | 190000 | 31666.6667 | 0.031667 | 600 | 0.6 | 1200000 | 1.2 | 1200 | 4.32 | 5.5517 | 0.39655 | 78.591 | 26.3972 | 0 | 0
2015-03-02 | 0 | 0 | 0.45 | 104.8 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 78.8996 | 26.7058 | 0 | 0
2015-03-03 | 0 | 0 | 0.45 | 104.35 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 79.2082 | 27.0143 | 0 | 0
2015-03-04 | 0.4 | 0.04 | 0.45 | 103.94 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 79.5461 | 27.3522 | 0 | 0
2015-03-05 | 1.8 | 0.18 | 0.45 | 103.67 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 79.9866 | 27.7928 | 0 | 0
2015-03-06 | 0.8 | 0.08 | 0.45 | 103.3 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 80.3538 | 28.16 | 0 | 0
2015-03-07 | 0 | 0 | 0.45 | 102.85 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 80.6624 | 28.4686 | 0 | 0
2015-03-08 | 0.4 | 0.04 | 0.45 | 102.44 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 81.0003 | 28.8064 | 0 | 0
2015-03-09 | 0.4 | 0.04 | 0.45 | 102.03 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 81.3382 | 29.1443 | 0 | 0
2015-03-10 | 2.8 | 0.28 | 0.45 | 101.86 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 81.852 | 29.6582 | 0 | 0
2015-03-11 | 13.6 | 1.36 | 0.45 | 102.77 | 190000 | 358888.8889 | 0.35889 | 6800 | 6.8 | 13600000 | 13.6 | 1200 | 4.32 | 18.2789 | 1.3056 | 83.1577 | 30.9638 | 0 | 0
2015-03-12 | 8.6 | 0.86 | 0.45 | 103.18 | 190000 | 226944.4444 | 0.22694 | 4300 | 4.3 | 8600000 | 8.6 | 1200 | 4.32 | 13.1469 | 0.93907 | 84.0967 | 31.9029 | 0 | 0
2015-03-13 | 17.4 | 1.74 | 0.45 | 104.47 | 190000 | 459166.6667 | 0.45917 | 8700 | 8.7 | 17400000 | 17.4 | 1200 | 4.32 | 22.1792 | 1.5842 | 85.681 | 33.4871 | 0 | 0
2015-03-14 | 0.6 | 0.06 | 0.45 | 104.08 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 86.0335 | 33.8397 | 0 | 0
2015-03-15 | 0 | 0 | 0.45 | 103.63 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 86.3421 | 34.1483 | 0 | 0
2015-03-16 | 0 | 0 | 0.45 | 103.18 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 86.6507 | 34.4568 | 0 | 0
2015-03-17 | 0 | 0 | 0.45 | 102.73 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 86.9592 | 34.7654 | 0 | 0
2015-03-18 | 31 | 2.5 | 0.45 | 104.78 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 89.1007 | 36.9068 | 0 | 0
2015-03-19 | 35.4 | 2.5 | 0.45 | 106.83 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 91.2421 | 39.0482 | 0 | 0
2015-03-20 | 28.6 | 2.5 | 0.45 | 108.88 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 93.3835 | 41.1896 | 0 | 0
2015-03-21 | 0 | 0 | 0.45 | 108.43 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 93.692 | 41.4982 | 0 | 0
2015-03-22 | 7 | 0.7 | 0.45 | 108.68 | 190000 | 184722.2222 | 0.18472 | 3500 | 3.5 | 7000000 | 7 | 1200 | 4.32 | 11.5047 | 0.82177 | 94.5138 | 42.32 | 0 | 0
2015-03-23 | 9.6 | 0.96 | 0.45 | 109.19 | 190000 | 253333.3333 | 0.25333 | 4800 | 4.8 | 9600000 | 9.6 | 1200 | 4.32 | 14.1733 | 1.0124 | 95.5262 | 43.3323 | 0 | 0
2015-03-24 | 18.2 | 1.82 | 0.45 | 110.56 | 190000 | 480277.7778 | 0.48028 | 9100 | 9.1 | 18200000 | 18.2 | 1200 | 4.32 | 23.0003 | 1.6429 | 97.1691 | 44.9752 | 0 | 0
2015-03-25 | 104.4 | 2.5 | 0.45 | 112.61 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 99.3105 | 47.1166 | 0 | 0
2015-03-26 | 33.2 | 2.5 | 0.45 | 114.66 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 101.4519 | 49.258 | 0 | 0
2015-03-27 | 26.2 | 2.5 | 0.45 | 116.71 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 103.5933 | 51.3994 | 0 | 0
2015-03-28 | 68.8 | 2.5 | 0.45 | 118.76 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 105.7347 | 53.5409 | 0 | 0
2015-03-29 | 10 | 1 | 0.45 | 119.31 | 190000 | 263888.8889 | 0.26389 | 5000 | 5 | 10000000 | 10 | 1200 | 4.32 | 14.5839 | 1.0417 | 106.7764 | 54.5826 | 0 | 0
2015-03-30 | 37.7 | 2.5 | 0.45 | 121.36 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 108.9178 | 56.724 | 0 | 0
2015-03-31 | 11.6 | 1.16 | 0.45 | 122.07 | 190000 | 306111.1111 | 0.30611 | 5800 | 5.8 | 11600000 | 11.6 | 1200 | 4.32 | 16.2261 | 1.159 | 110.0768 | 57.883 | 0 | 0
2015-04-01 | 0 | 0 | 0.45 | 121.62 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 110.3854 | 58.1915 | 0 | 0
2015-04-02 | 33.7 | 2.5 | 0.45 | 123.67 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 112.5268 | 60.333 | 0 | 0
2015-04-03 | 9 | 0.9 | 0.45 | 124.12 | 190000 | 237500 | 0.2375 | 4500 | 4.5 | 9000000 | 9 | 1200 | 4.32 | 13.5575 | 0.96839 | 113.4952 | 61.3013 | 0 | 0
2015-04-04 | 8.4 | 0.84 | 0.45 | 124.51 | 190000 | 221666.6667 | 0.22167 | 4200 | 4.2 | 8400000 | 8.4 | 1200 | 4.32 | 12.9417 | 0.9244 | 114.4196 | 62.2258 | 0 | 0
2015-04-05 | 0.6 | 0.06 | 0.45 | 124.12 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 114.7722 | 62.5783 | 0 | 0
2015-04-06 | 0 | 0 | 0.45 | 123.67 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 115.0807 | 62.8869 | 0 | 0
2015-04-07 | 0 | 0 | 0.45 | 123.22 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 115.3893 | 63.1955 | 0 | 0
2015-04-08 | 0 | 0 | 0.45 | 122.77 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 115.6979 | 63.504 | 0 | 0
2015-04-09 | 3.2 | 0.32 | 0.45 | 122.64 | 190000 | 84444.4444 | 0.084444 | 1600 | 1.6 | 3200000 | 3.2 | 1200 | 4.32 | 7.6044 | 0.54317 | 116.2411 | 64.0472 | 0 | 0
2015-04-10 | 40.2 | 2.5 | 0.45 | 124.69 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 118.3825 | 66.1886 | 0 | 0
2015-04-11 | 9.2 | 0.92 | 0.45 | 125.16 | 190000 | 242777.7778 | 0.24278 | 4600 | 4.6 | 9200000 | 9.2 | 1200 | 4.32 | 13.7628 | 0.98306 | 119.3655 | 67.1717 | 0 | 0
2015-04-12 | 24.4 | 2.44 | 0.45 | 127.15 | 190000 | 643888.8889 | 0.64389 | 12200 | 12.2 | 24400000 | 24.4 | 1200 | 4.32 | 29.3639 | 2.0974 | 121.4629 | 69.2691 | 0 | 0
2015-04-13 | 16.2 | 1.62 | 0.45 | 128.32 | 190000 | 427500 | 0.4275 | 8100 | 8.1 | 16200000 | 16.2 | 1200 | 4.32 | 20.9475 | 1.4962 | 122.9592 | 70.7653 | 0 | 0
2015-04-14 | 1.5 | 0.15 | 0.45 | 128.02 | 190000 | 39583.3333 | 0.039583 | 750 | 0.75 | 1500000 | 1.5 | 1200 | 4.32 | 5.8596 | 0.41854 | 123.3777 | 71.1839 | 0 | 0
2015-04-15 | 37.2 | 2.5 | 0.45 | 130.07 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 125.5191 | 73.3253 | 0 | 0
2015-04-16 | 3 | 0.3 | 0.45 | 129.92 | 190000 | 79166.6667 | 0.079167 | 1500 | 1.5 | 3000000 | 3 | 1200 | 4.32 | 7.3992 | 0.52851 | 126.0476 | 73.8538 | 0 | 0
2015-04-17 | 0 | 0 | 0.45 | 129.47 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 126.3562 | 74.1624 | 0 | 0
2015-04-18 | 0 | 0 | 0.45 | 129.02 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 126.6648 | 74.4709 | 0 | 0
2015-04-19 | 0 | 0 | 0.45 | 128.57 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 126.9734 | 74.7795 | 0 | 0
2015-04-20 | 1.1 | 0.11 | 0.45 | 128.23 | 190000 | 29027.7778 | 0.029028 | 550 | 0.55 | 1100000 | 1.1 | 1200 | 4.32 | 5.449 | 0.38922 | 127.3626 | 75.1687 | 0 | 0
2015-04-21 | 0.4 | 0.04 | 0.45 | 127.82 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 127.7005 | 75.5066 | 0 | 0
2015-04-22 | 8.2 | 0.82 | 0.45 | 128.19 | 190000 | 216388.8889 | 0.21639 | 4100 | 4.1 | 8200000 | 8.2 | 1200 | 4.32 | 12.7364 | 0.90974 | 128.6102 | 76.4164 | 0 | 0
2015-04-23 | 8.4 | 0.84 | 0.45 | 128.58 | 190000 | 221666.6667 | 0.22167 | 4200 | 4.2 | 8400000 | 8.4 | 1200 | 4.32 | 12.9417 | 0.9244 | 129.5346 | 77.3408 | 0 | 0
2015-04-24 | 1.8 | 0.18 | 0.45 | 128.31 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 129.9752 | 77.7813 | 0 | 0
2015-04-25 | 0 | 0 | 0.45 | 127.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 130.2837 | 78.0899 | 0 | 0
2015-04-26 | 4.2 | 0.42 | 0.45 | 127.83 | 190000 | 110833.3333 | 0.11083 | 2100 | 2.1 | 4200000 | 4.2 | 1200 | 4.32 | 8.6308 | 0.61649 | 130.9002 | 78.7064 | 0 | 0
2015-04-27 | 22.4 | 2.24 | 0.45 | 129.62 | 190000 | 591111.1111 | 0.59111 | 11200 | 11.2 | 22400000 | 22.4 | 1200 | 4.32 | 27.3111 | 1.9508 | 132.851 | 80.6572 | 0 | 0
2015-04-28 | 15.4 | 1.54 | 0.45 | 130.71 | 190000 | 406388.8889 | 0.40639 | 7700 | 7.7 | 15400000 | 15.4 | 1200 | 4.32 | 20.1264 | 1.4376 | 134.2886 | 82.0948 | 0 | 0
2015-04-29 | 27.6 | 2.5 | 0.45 | 132.76 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 136.43 | 84.2362 | 0 | 0
2015-04-30 | 4.8 | 0.48 | 0.45 | 132.79 | 190000 | 126666.6667 | 0.12667 | 2400 | 2.4 | 4800000 | 4.8 | 1200 | 4.32 | 9.2467 | 0.66048 | 137.0905 | 84.8966 | 0 | 0
2015-05-01 | 0.8 | 0.08 | 0.45 | 132.42 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 137.4577 | 85.2639 | 0 | 0
2015-05-02 | 0 | 0 | 0.45 | 131.97 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 137.7663 | 85.5724 | 0 | 0
2015-05-03 | 0 | 0 | 0.45 | 131.52 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 138.0749 | 85.881 | 0 | 0
2015-05-04 | 19.8 | 1.98 | 0.45 | 133.05 | 190000 | 522500 | 0.5225 | 9900 | 9.9 | 19800000 | 19.8 | 1200 | 4.32 | 24.6425 | 1.7602 | 139.835 | 87.6412 | 0 | 0
2015-05-05 | 0.4 | 0.04 | 0.45 | 132.64 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 140.1729 | 87.9791 | 0 | 0
2015-05-06 | 0 | 0 | 0.45 | 132.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 140.4815 | 88.2877 | 0 | 0
2015-05-07 | 0 | 0 | 0.45 | 131.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 140.7901 | 88.5962 | 0 | 0
2015-05-08 | 0 | 0 | 0.45 | 131.29 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 141.0987 | 88.9048 | 0 | 0
2015-05-09 | 0 | 0 | 0.45 | 130.84 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 141.4072 | 89.2134 | 0 | 0
2015-05-10 | 0.4 | 0.04 | 0.45 | 130.43 | 190000 | 10555.5556 | 0.010556 | 200 | 0.2 | 400000 | 0.4 | 1200 | 4.32 | 4.7306 | 0.3379 | 141.7451 | 89.5513 | 0 | 0
2015-05-11 | 0 | 0 | 0.45 | 129.98 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 142.0537 | 89.8598 | 0 | 0
2015-05-12 | 0 | 0 | 0.45 | 129.53 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 142.3623 | 90.1684 | 0 | 0
2015-05-13 | 0 | 0 | 0.45 | 129.08 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 142.6708 | 90.477 | 0 | 0
2015-05-14 | 0 | 0 | 0.45 | 128.63 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 142.9794 | 90.7856 | 0 | 0
2015-05-15 | 0 | 0 | 0.45 | 128.18 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 143.288 | 91.0941 | 0 | 0
2015-05-16 | 0.2 | 0.02 | 0.45 | 127.75 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 143.6112 | 91.4174 | 0 | 0
2015-05-17 | 0 | 0 | 0.45 | 127.3 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 143.9198 | 91.7259 | 0 | 0
2015-05-18 | 0 | 0 | 0.45 | 126.85 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 144.2284 | 92.0345 | 0 | 0
2015-05-19 | 0 | 0 | 0.45 | 126.4 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 144.5369 | 92.3431 | 0 | 0
2015-05-20 | 0 | 0 | 0.45 | 125.95 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 144.8455 | 92.6516 | 0 | 0
2015-05-21 | 0 | 0 | 0.45 | 125.5 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 145.1541 | 92.9602 | 0 | 0
2015-05-22 | 0.2 | 0.02 | 0.45 | 125.07 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 145.4773 | 93.2835 | 0 | 0
2015-05-23 | 0.2 | 0.02 | 0.45 | 124.64 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 145.8005 | 93.6067 | 0 | 0
2015-05-24 | 0 | 0 | 0.45 | 124.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 146.1091 | 93.9153 | 0 | 0
2015-05-25 | 0 | 0 | 0.45 | 123.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 146.4177 | 94.2238 | 0 | 0
2015-05-26 | 0 | 0 | 0.45 | 123.29 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 146.7263 | 94.5324 | 0 | 0
2015-05-27 | 0 | 0 | 0.45 | 122.84 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 147.0348 | 94.841 | 0 | 0
2015-05-28 | 0 | 0 | 0.45 | 122.39 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 147.3434 | 95.1495 | 0 | 0
2015-05-29 | 0 | 0 | 0.45 | 121.94 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 147.652 | 95.4581 | 0 | 0
2015-05-30 | 0 | 0 | 0.45 | 121.49 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 147.9605 | 95.7667 | 0 | 0
2015-05-31 | 0 | 0 | 0.45 | 121.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 148.2691 | 96.0753 | 0 | 0
2015-06-01 | 7.4 | 0.74 | 0.45 | 121.33 | 190000 | 195277.7778 | 0.19528 | 3700 | 3.7 | 7400000 | 7.4 | 1200 | 4.32 | 11.9153 | 0.85109 | 149.1202 | 96.9263 | 0 | 0
2015-06-02 | 2.8 | 0.28 | 0.45 | 121.16 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 149.634 | 97.4402 | 0 | 0
2015-06-03 | 0 | 0 | 0.45 | 120.71 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 149.9426 | 97.7488 | 0 | 0
2015-06-04 | 0 | 0 | 0.45 | 120.26 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 150.2512 | 98.0573 | 0 | 0
2015-06-05 | 0 | 0 | 0.45 | 119.81 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 150.5598 | 98.3659 | 0 | 0
2015-06-06 | 0 | 0 | 0.45 | 119.36 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 150.8683 | 98.6745 | 0 | 0
2015-06-07 | 0 | 0 | 0.45 | 118.91 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.1769 | 98.9831 | 0 | 0
2015-06-08 | 0 | 0 | 0.45 | 118.46 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.4855 | 99.2916 | 0 | 0
2015-06-09 | 0 | 0 | 0.45 | 118.01 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 151.794 | 99.6002 | 0 | 0
2015-06-10 | 0 | 0 | 0.45 | 117.56 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 152.1026 | 99.9088 | 0 | 0
2015-06-11 | 0 | 0 | 0.45 | 117.11 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 152.4112 | 0 | 0 | 1
2015-06-12 | 0 | 0 | 0.45 | 116.66 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 152.7198 | 0.30857 | 0 | 0
2015-06-13 | 0 | 0 | 0.45 | 116.21 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.0283 | 0.61714 | 0 | 0
2015-06-14 | 0 | 0 | 0.45 | 115.76 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.3369 | 0.92571 | 0 | 0
2015-06-15 | 0 | 0 | 0.45 | 115.31 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.6455 | 1.2343 | 0 | 0
2015-06-16 | 0 | 0 | 0.45 | 114.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 153.954 | 1.5429 | 0 | 0
2015-06-17 | 0 | 0 | 0.45 | 114.41 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 154.2626 | 1.8514 | 0 | 0
2015-06-18 | 7 | 0.7 | 0.45 | 114.66 | 190000 | 184722.2222 | 0.18472 | 3500 | 3.5 | 7000000 | 7 | 1200 | 4.32 | 11.5047 | 0.82177 | 155.0844 | 2.6732 | 0 | 0
2015-06-19 | 0 | 0 | 0.45 | 114.21 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 155.393 | 2.9818 | 0 | 0
2015-06-20 | 0 | 0 | 0.45 | 113.76 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 155.7015 | 3.2903 | 0 | 0
2015-06-21 | 0 | 0 | 0.45 | 113.31 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 156.0101 | 3.5989 | 0 | 0
2015-06-22 | 0 | 0 | 0.45 | 112.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 156.3187 | 3.9075 | 0 | 0
2015-06-23 | 1.4 | 0.14 | 0.45 | 112.55 | 190000 | 36944.4444 | 0.036944 | 700 | 0.7 | 1400000 | 1.4 | 1200 | 4.32 | 5.7569 | 0.41121 | 156.7299 | 4.3187 | 0 | 0
2015-06-24 | 13.4 | 1.34 | 0.45 | 113.44 | 190000 | 353611.1111 | 0.35361 | 6700 | 6.7 | 13400000 | 13.4 | 1200 | 4.32 | 18.0736 | 1.291 | 158.0209 | 5.6097 | 0 | 0
2015-06-25 | 4 | 0.4 | 0.45 | 113.39 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 158.6227 | 6.2115 | 0 | 0
2015-06-26 | 0 | 0 | 0.45 | 112.94 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 158.9313 | 6.5201 | 0 | 0
2015-06-27 | 0 | 0 | 0.45 | 112.49 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 159.2398 | 6.8286 | 0 | 0
2015-06-28 | 0 | 0 | 0.45 | 112.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 159.5484 | 7.1372 | 0 | 0
2015-06-29 | 0 | 0 | 0.45 | 111.59 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 159.857 | 7.4458 | 0 | 0
2015-06-30 | 0 | 0 | 0.45 | 111.14 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 160.1655 | 7.7543 | 0 | 0
2015-07-01 | 0 | 0 | 0.45 | 110.69 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 160.4741 | 8.0629 | 0 | 0
2015-07-02 | 0 | 0 | 0.45 | 110.24 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 160.7827 | 8.3715 | 0 | 0
2015-07-03 | 0 | 0 | 0.45 | 109.79 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 161.0913 | 8.6801 | 0 | 0
2015-07-04 | 0 | 0 | 0.45 | 109.34 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 161.3998 | 8.9886 | 0 | 0
2015-07-05 | 0 | 0 | 0.45 | 108.89 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 161.7084 | 9.2972 | 0 | 0
2015-07-06 | 0 | 0 | 0.45 | 108.44 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 162.017 | 9.6058 | 0 | 0
2015-07-07 | 0.2 | 0.02 | 0.45 | 108.01 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 162.3402 | 9.929 | 0 | 0
2015-07-08 | 0 | 0 | 0.45 | 107.56 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 162.6488 | 10.2376 | 0 | 0
2015-07-09 | 1 | 0.1 | 0.45 | 107.21 | 190000 | 26388.8889 | 0.026389 | 500 | 0.5 | 1000000 | 1 | 1200 | 4.32 | 5.3464 | 0.38188 | 163.0307 | 10.6195 | 0 | 0
2015-07-10 | 1.2 | 0.12 | 0.45 | 106.88 | 190000 | 31666.6667 | 0.031667 | 600 | 0.6 | 1200000 | 1.2 | 1200 | 4.32 | 5.5517 | 0.39655 | 163.4272 | 11.016 | 0 | 0
2015-07-11 | 2.4 | 0.24 | 0.45 | 106.67 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 163.9117 | 11.5005 | 0 | 0
2015-07-12 | 4 | 0.4 | 0.45 | 106.62 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 164.5136 | 12.1024 | 0 | 0
2015-07-13 | 0 | 0 | 0.45 | 106.17 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 164.8221 | 12.4109 | 0 | 0
2015-07-14 | 0 | 0 | 0.45 | 105.72 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.1307 | 12.7195 | 0 | 0
2015-07-15 | 0 | 0 | 0.45 | 105.27 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.4393 | 13.0281 | 0 | 0
2015-07-16 | 0 | 0 | 0.45 | 104.82 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 165.7478 | 13.3366 | 0 | 0
2015-07-17 | 0 | 0 | 0.45 | 104.37 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 166.0564 | 13.6452 | 0 | 0
2015-07-18 | 0 | 0 | 0.45 | 103.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 166.365 | 13.9538 | 0 | 0
2015-07-19 | 0 | 0 | 0.45 | 103.47 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 166.6736 | 14.2624 | 0 | 0
2015-07-20 | 0.6 | 0.06 | 0.45 | 103.08 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 167.0261 | 14.6149 | 0 | 0
2015-07-21 | 0 | 0 | 0.45 | 102.63 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 167.3347 | 14.9235 | 0 | 0
2015-07-22 | 0 | 0 | 0.45 | 102.18 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 167.6433 | 15.2321 | 0 | 0
2015-07-23 | 8.4 | 0.84 | 0.45 | 102.57 | 190000 | 221666.6667 | 0.22167 | 4200 | 4.2 | 8400000 | 8.4 | 1200 | 4.32 | 12.9417 | 0.9244 | 168.5677 | 16.1565 | 0 | 0
2015-07-24 | 4 | 0.4 | 0.45 | 102.52 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 169.1695 | 16.7583 | 0 | 0
2015-07-25 | 4.2 | 0.42 | 0.45 | 102.49 | 190000 | 110833.3333 | 0.11083 | 2100 | 2.1 | 4200000 | 4.2 | 1200 | 4.32 | 8.6308 | 0.61649 | 169.786 | 17.3748 | 0 | 0
2015-07-26 | 0 | 0 | 0.45 | 102.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 170.0945 | 17.6834 | 0 | 0
2015-07-27 | 0 | 0 | 0.45 | 101.59 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 170.4031 | 17.9919 | 0 | 0
2015-07-28 | 0 | 0 | 0.45 | 101.14 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 170.7117 | 18.3005 | 0 | 0
2015-07-29 | 0 | 0 | 0.45 | 100.69 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 171.0203 | 18.6091 | 0 | 0
2015-07-30 | 0 | 0 | 0.45 | 100.24 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 171.3288 | 18.9176 | 0 | 0
2015-07-31 | 0 | 0 | 0.45 | 99.79 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 171.6374 | 19.2262 | 0 | 0
2015-08-01 | 0 | 0 | 0.45 | 99.34 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 171.946 | 19.5348 | 0 | 0
2015-08-02 | 0 | 0 | 0.45 | 98.89 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 172.2545 | 19.8434 | 0 | 0
2015-08-03 | 0 | 0 | 0.45 | 98.44 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 172.5631 | 20.1519 | 0 | 0
2015-08-04 | 0 | 0 | 0.45 | 97.99 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 172.8717 | 20.4605 | 0 | 0
2015-08-05 | 0 | 0 | 0.45 | 97.54 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 173.1803 | 20.7691 | 0 | 0
2015-08-06 | 3.2 | 0.32 | 0.45 | 97.41 | 190000 | 84444.4444 | 0.084444 | 1600 | 1.6 | 3200000 | 3.2 | 1200 | 4.32 | 7.6044 | 0.54317 | 173.7234 | 21.3122 | 0 | 0
2015-08-07 | 14.6 | 1.46 | 0.45 | 98.42 | 190000 | 385277.7778 | 0.38528 | 7300 | 7.3 | 14600000 | 14.6 | 1200 | 4.32 | 19.3053 | 1.3789 | 175.1024 | 22.6912 | 0 | 0
2015-08-08 | 24.4 | 2.44 | 0.45 | 100.41 | 190000 | 643888.8889 | 0.64389 | 12200 | 12.2 | 24400000 | 24.4 | 1200 | 4.32 | 29.3639 | 2.0974 | 177.1998 | 24.7886 | 0 | 0
2015-08-09 | 1.8 | 0.18 | 0.45 | 100.14 | 190000 | 47500 | 0.0475 | 900 | 0.9 | 1800000 | 1.8 | 1200 | 4.32 | 6.1675 | 0.44054 | 177.6403 | 25.2291 | 0 | 0
2015-08-10 | 0 | 0 | 0.45 | 99.69 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 177.9489 | 25.5377 | 0 | 0
2015-08-11 | 0 | 0 | 0.45 | 99.24 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 178.2575 | 25.8463 | 0 | 0
2015-08-12 | 0 | 0 | 0.45 | 98.79 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 178.5661 | 26.1549 | 0 | 0
2015-08-13 | 0 | 0 | 0.45 | 98.34 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 178.8746 | 26.4634 | 0 | 0
2015-08-14 | 0 | 0 | 0.45 | 97.89 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 179.1832 | 26.772 | 0 | 0
2015-08-15 | 0 | 0 | 0.45 | 97.44 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 179.4918 | 27.0806 | 0 | 0
2015-08-16 | 0 | 0 | 0.45 | 96.99 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 179.8003 | 27.3891 | 0 | 0
2015-08-17 | 0 | 0 | 0.45 | 96.54 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 180.1089 | 27.6977 | 0 | 0
2015-08-18 | 0 | 0 | 0.45 | 96.09 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 180.4175 | 28.0063 | 0 | 0
2015-08-19 | 0 | 0 | 0.45 | 95.64 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 180.7261 | 28.3149 | 0 | 0
2015-08-20 | 0 | 0 | 0.45 | 95.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 181.0346 | 28.6234 | 0 | 0
2015-08-21 | 0 | 0 | 0.45 | 94.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 181.3432 | 28.932 | 0 | 0
2015-08-22 | 0 | 0 | 0.45 | 94.29 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 181.6518 | 29.2406 | 0 | 0
2015-08-23 | 0 | 0 | 0.45 | 93.84 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 181.9603 | 29.5491 | 0 | 0
2015-08-24 | 0 | 0 | 0.45 | 93.39 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 182.2689 | 29.8577 | 0 | 0
2015-08-25 | 0 | 0 | 0.45 | 92.94 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 182.5775 | 30.1663 | 0 | 0
2015-08-26 | 0 | 0 | 0.45 | 92.49 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 182.8861 | 30.4749 | 0 | 0
2015-08-27 | 2.8 | 0.28 | 0.45 | 92.32 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 183.3999 | 30.9887 | 0 | 0
2015-08-28 | 10.4 | 1.04 | 0.45 | 92.91 | 190000 | 274444.4444 | 0.27444 | 5200 | 5.2 | 10400000 | 10.4 | 1200 | 4.32 | 14.9944 | 1.071 | 184.4709 | 32.0597 | 0 | 0
2015-08-29 | 33.4 | 2.5 | 0.45 | 94.96 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 186.6123 | 34.2012 | 0 | 0
2015-08-30 | 26 | 2.5 | 0.45 | 97.01 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 188.7538 | 36.3426 | 0 | 0
2015-08-31 | 6 | 0.6 | 0.45 | 97.16 | 190000 | 158333.3333 | 0.15833 | 3000 | 3 | 6000000 | 6 | 1200 | 4.32 | 10.4783 | 0.74845 | 189.5022 | 37.091 | 0 | 0
2015-09-01 | 15.8 | 1.58 | 0.45 | 98.29 | 190000 | 416944.4444 | 0.41694 | 7900 | 7.9 | 15800000 | 15.8 | 1200 | 4.32 | 20.5369 | 1.4669 | 190.9691 | 38.5579 | 0 | 0
2015-09-02 | 0.8 | 0.08 | 0.45 | 97.92 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 191.3363 | 38.9252 | 0 | 0
2015-09-03 | 2.4 | 0.24 | 0.45 | 97.71 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 191.8209 | 39.4097 | 0 | 0
2015-09-04 | 0 | 0 | 0.45 | 97.26 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 192.1294 | 39.7183 | 0 | 0
2015-09-05 | 1.6 | 0.16 | 0.45 | 96.97 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 192.5553 | 40.1441 | 0 | 0
2015-09-06 | 0 | 0 | 0.45 | 96.52 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 192.8639 | 40.4527 | 0 | 0
2015-09-07 | 29.6 | 2.5 | 0.45 | 98.57 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 195.0053 | 42.5941 | 0 | 0
2015-09-08 | 13 | 1.3 | 0.45 | 99.42 | 190000 | 343055.5556 | 0.34306 | 6500 | 6.5 | 13000000 | 13 | 1200 | 4.32 | 17.6631 | 1.2616 | 196.2669 | 43.8558 | 0 | 0
2015-09-09 | 1.4 | 0.14 | 0.45 | 99.11 | 190000 | 36944.4444 | 0.036944 | 700 | 0.7 | 1400000 | 1.4 | 1200 | 4.32 | 5.7569 | 0.41121 | 196.6782 | 44.267 | 0 | 0
2015-09-10 | 0 | 0 | 0.45 | 98.66 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 196.9867 | 44.5755 | 0 | 0
2015-09-11 | 0 | 0 | 0.45 | 98.21 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 197.2953 | 44.8841 | 0 | 0
2015-09-12 | 0 | 0 | 0.45 | 97.76 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 197.6039 | 45.1927 | 0 | 0
2015-09-13 | 0 | 0 | 0.45 | 97.31 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 197.9124 | 45.5012 | 0 | 0
2015-09-14 | 0 | 0 | 0.45 | 96.86 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 198.221 | 45.8098 | 0 | 0
2015-09-15 | 2 | 0.2 | 0.45 | 96.61 | 190000 | 52777.7778 | 0.052778 | 1000 | 1 | 2000000 | 2 | 1200 | 4.32 | 6.3728 | 0.4552 | 198.6762 | 46.265 | 0 | 0
2015-09-16 | 4 | 0.4 | 0.45 | 96.56 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 199.278 | 46.8668 | 0 | 0
2015-09-17 | 2.8 | 0.28 | 0.45 | 96.39 | 190000 | 73888.8889 | 0.073889 | 1400 | 1.4 | 2800000 | 2.8 | 1200 | 4.32 | 7.1939 | 0.51385 | 199.7919 | 47.3807 | 0 | 0
2015-09-18 | 46.4 | 2.5 | 0.45 | 98.44 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 201.9333 | 49.5221 | 0 | 0
2015-09-19 | 86.8 | 2.5 | 0.45 | 100.49 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 204.0747 | 51.6635 | 0 | 0
2015-09-20 | 1.4 | 0.14 | 0.45 | 100.18 | 190000 | 36944.4444 | 0.036944 | 700 | 0.7 | 1400000 | 1.4 | 1200 | 4.32 | 5.7569 | 0.41121 | 204.4859 | 52.0747 | 0 | 0
2015-09-21 | 4.2 | 0.42 | 0.45 | 100.15 | 190000 | 110833.3333 | 0.11083 | 2100 | 2.1 | 4200000 | 4.2 | 1200 | 4.32 | 8.6308 | 0.61649 | 205.1024 | 52.6912 | 0 | 0
2015-09-22 | 39.8 | 2.5 | 0.45 | 102.2 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 207.2438 | 54.8326 | 0 | 0
2015-09-23 | 29.8 | 2.5 | 0.45 | 104.25 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 209.3852 | 56.974 | 0 | 0
2015-09-24 | 11.8 | 1.18 | 0.45 | 104.98 | 190000 | 311388.8889 | 0.31139 | 5900 | 5.9 | 11800000 | 11.8 | 1200 | 4.32 | 16.4314 | 1.1737 | 210.5589 | 58.1477 | 0 | 0
2015-09-25 | 1.6 | 0.16 | 0.45 | 104.69 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 210.9848 | 58.5736 | 0 | 0
2015-09-26 | 0 | 0 | 0.45 | 104.24 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 211.2933 | 58.8821 | 0 | 0
2015-09-27 | 0 | 0 | 0.45 | 103.79 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 211.6019 | 59.1907 | 0 | 0
2015-09-28 | 0 | 0 | 0.45 | 103.34 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 211.9105 | 59.4993 | 0 | 0
2015-09-29 | 0 | 0 | 0.45 | 102.89 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 212.219 | 59.8079 | 0 | 0
2015-09-30 | 0 | 0 | 0.45 | 102.44 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 212.5276 | 60.1164 | 0 | 0
2015-10-01 | 0 | 0 | 0.45 | 101.99 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 212.8362 | 60.425 | 0 | 0
2015-10-02 | 0 | 0 | 0.45 | 101.54 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 213.1448 | 60.7336 | 0 | 0
2015-10-03 | 0 | 0 | 0.45 | 101.09 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 213.4533 | 61.0421 | 0 | 0
2015-10-04 | 0 | 0 | 0.45 | 100.64 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 213.7619 | 61.3507 | 0 | 0
2015-10-05 | 0 | 0 | 0.45 | 100.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 214.0705 | 61.6593 | 0 | 0
2015-10-06 | 4 | 0.4 | 0.45 | 100.14 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 214.6723 | 62.2611 | 0 | 0
2015-10-07 | 15.6 | 1.56 | 0.45 | 101.25 | 190000 | 411666.6667 | 0.41167 | 7800 | 7.8 | 15600000 | 15.6 | 1200 | 4.32 | 20.3317 | 1.4523 | 216.1246 | 63.7134 | 0 | 0
2015-10-08 | 9.2 | 0.92 | 0.45 | 101.72 | 190000 | 242777.7778 | 0.24278 | 4600 | 4.6 | 9200000 | 9.2 | 1200 | 4.32 | 13.7628 | 0.98306 | 217.1076 | 64.6964 | 0 | 0
2015-10-09 | 26.4 | 2.5 | 0.45 | 103.77 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 219.249 | 66.8378 | 0 | 0
2015-10-10 | 27 | 2.5 | 0.45 | 105.82 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 221.3904 | 68.9792 | 0 | 0
2015-10-11 | 37.6 | 2.5 | 0.45 | 107.87 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 223.5318 | 71.1207 | 0 | 0
2015-10-12 | 0.8 | 0.08 | 0.45 | 107.5 | 190000 | 21111.1111 | 0.021111 | 400 | 0.4 | 800000 | 0.8 | 1200 | 4.32 | 5.1411 | 0.36722 | 223.8991 | 71.4879 | 0 | 0
2015-10-13 | 0.6 | 0.06 | 0.45 | 107.11 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 224.2516 | 71.8404 | 0 | 0
2015-10-14 | 0 | 0 | 0.45 | 106.66 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 224.5602 | 72.149 | 0 | 0
2015-10-15 | 0 | 0 | 0.45 | 106.21 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 224.8688 | 72.4576 | 0 | 0
2015-10-16 | 14.2 | 1.42 | 0.45 | 107.18 | 190000 | 374722.2222 | 0.37472 | 7100 | 7.1 | 14200000 | 14.2 | 1200 | 4.32 | 18.8947 | 1.3496 | 226.2184 | 73.8072 | 0 | 0
2015-10-17 | 6.4 | 0.64 | 0.45 | 107.37 | 190000 | 168888.8889 | 0.16889 | 3200 | 3.2 | 6400000 | 6.4 | 1200 | 4.32 | 10.8889 | 0.77778 | 226.9962 | 74.585 | 0 | 0
2015-10-18 | 23.4 | 2.34 | 0.45 | 109.26 | 190000 | 617500 | 0.6175 | 11700 | 11.7 | 23400000 | 23.4 | 1200 | 4.32 | 28.3375 | 2.0241 | 229.0203 | 76.6091 | 0 | 0
2015-10-19 | 0.6 | 0.06 | 0.45 | 108.87 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 229.3728 | 76.9616 | 0 | 0
2015-10-20 | 10.2 | 1.02 | 0.45 | 109.44 | 190000 | 269166.6667 | 0.26917 | 5100 | 5.1 | 10200000 | 10.2 | 1200 | 4.32 | 14.7892 | 1.0564 | 230.4292 | 78.018 | 0 | 0
2015-10-21 | 4 | 0.4 | 0.45 | 109.39 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 231.031 | 78.6198 | 0 | 0
2015-10-22 | 9.8 | 0.98 | 0.45 | 109.92 | 190000 | 258611.1111 | 0.25861 | 4900 | 4.9 | 9800000 | 9.8 | 1200 | 4.32 | 14.3786 | 1.027 | 232.0581 | 79.6469 | 0 | 0
2015-10-23 | 0 | 0 | 0.45 | 109.47 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 232.3666 | 79.9555 | 0 | 0
2015-10-24 | 5.8 | 0.58 | 0.45 | 109.6 | 190000 | 153055.5556 | 0.15306 | 2900 | 2.9 | 5800000 | 5.8 | 1200 | 4.32 | 10.2731 | 0.73379 | 233.1004 | 80.6892 | 0 | 0
2015-10-25 | 4 | 0.4 | 0.45 | 109.55 | 190000 | 105555.5556 | 0.10556 | 2000 | 2 | 4000000 | 4 | 1200 | 4.32 | 8.4256 | 0.60183 | 233.7023 | 81.2911 | 0 | 0
2015-10-26 | 0 | 0 | 0.45 | 109.1 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 234.0108 | 81.5996 | 0 | 0
2015-10-27 | 6.8 | 0.68 | 0.45 | 109.33 | 190000 | 179444.4444 | 0.17944 | 3400 | 3.4 | 6800000 | 6.8 | 1200 | 4.32 | 11.2994 | 0.8071 | 234.8179 | 82.4067 | 0 | 0
2015-10-28 | 39 | 2.5 | 0.45 | 111.38 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 236.9593 | 84.5482 | 0 | 0
2015-10-29 | 40.6 | 2.5 | 0.45 | 113.43 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 239.1008 | 86.6896 | 0 | 0
2015-10-30 | 35.4 | 2.5 | 0.45 | 115.48 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 241.2422 | 88.831 | 0 | 0
2015-10-31 | 21.2 | 2.12 | 0.45 | 117.15 | 190000 | 559444.4444 | 0.55944 | 10600 | 10.6 | 21200000 | 21.2 | 1200 | 4.32 | 26.0794 | 1.8628 | 243.105 | 90.6938 | 0 | 0
2015-11-01 | 1.2 | 0.12 | 0.45 | 116.82 | 190000 | 31666.6667 | 0.031667 | 600 | 0.6 | 1200000 | 1.2 | 1200 | 4.32 | 5.5517 | 0.39655 | 243.5015 | 91.0903 | 0 | 0
2015-11-02 | 0 | 0 | 0.45 | 116.37 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 243.8101 | 91.3989 | 0 | 0
2015-11-03 | 0 | 0 | 0.45 | 115.92 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 244.1187 | 91.7075 | 0 | 0
2015-11-04 | 3.4 | 0.34 | 0.45 | 115.81 | 190000 | 89722.2222 | 0.089722 | 1700 | 1.7 | 3400000 | 3.4 | 1200 | 4.32 | 7.8097 | 0.55784 | 244.6765 | 92.2653 | 0 | 0
2015-11-05 | 6 | 0.6 | 0.45 | 115.96 | 190000 | 158333.3333 | 0.15833 | 3000 | 3 | 6000000 | 6 | 1200 | 4.32 | 10.4783 | 0.74845 | 245.425 | 93.0138 | 0 | 0
2015-11-06 | 44.2 | 2.5 | 0.45 | 118.01 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 247.5664 | 95.1552 | 0 | 0
2015-11-07 | 2.2 | 0.22 | 0.45 | 117.78 | 190000 | 58055.5556 | 0.058056 | 1100 | 1.1 | 2200000 | 2.2 | 1200 | 4.32 | 6.5781 | 0.46986 | 248.0362 | 95.625 | 0 | 0
2015-11-08 | 1.6 | 0.16 | 0.45 | 117.49 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 248.4621 | 96.0509 | 0 | 0
2015-11-09 | 0 | 0 | 0.45 | 117.04 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 248.7707 | 96.3595 | 0 | 0
2015-11-10 | 20.5 | 2.05 | 0.45 | 118.64 | 190000 | 540972.2222 | 0.54097 | 10250 | 10.25 | 20500000 | 20.5 | 1200 | 4.32 | 25.361 | 1.8115 | 0 | 98.171 | 1 | 0
2015-11-11 | 18.8 | 1.88 | 0.45 | 120.07 | 190000 | 496111.1111 | 0.49611 | 9400 | 9.4 | 18800000 | 18.8 | 1200 | 4.32 | 23.6161 | 1.6869 | 1.6869 | 99.8578 | 0 | 0
2015-11-12 | 59 | 2.5 | 0.45 | 122.12 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 3.8283 | 0 | 0 | 1
2015-11-13 | 11.4 | 1.14 | 0.45 | 122.81 | 190000 | 300833.3333 | 0.30083 | 5700 | 5.7 | 11400000 | 11.4 | 1200 | 4.32 | 16.0208 | 1.1443 | 4.9726 | 1.1443 | 0 | 0
2015-11-14 | 0.6 | 0.06 | 0.45 | 122.42 | 190000 | 15833.3333 | 0.015833 | 300 | 0.3 | 600000 | 0.6 | 1200 | 4.32 | 4.9358 | 0.35256 | 5.3252 | 1.4969 | 0 | 0
2015-11-15 | 6 | 0.6 | 0.45 | 122.57 | 190000 | 158333.3333 | 0.15833 | 3000 | 3 | 6000000 | 6 | 1200 | 4.32 | 10.4783 | 0.74845 | 6.0736 | 2.2454 | 0 | 0
2015-11-16 | 55.4 | 2.5 | 0.45 | 124.62 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 8.215 | 4.3868 | 0 | 0
2015-11-17 | 6.2 | 0.62 | 0.45 | 124.79 | 190000 | 163611.1111 | 0.16361 | 3100 | 3.1 | 6200000 | 6.2 | 1200 | 4.32 | 10.6836 | 0.76312 | 8.9782 | 5.1499 | 0 | 0
2015-11-18 | 0 | 0 | 0.45 | 124.34 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 9.2867 | 5.4585 | 0 | 0
2015-11-19 | 0 | 0 | 0.45 | 123.89 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 9.5953 | 5.767 | 0 | 0
2015-11-20 | 0 | 0 | 0.45 | 123.44 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 9.9039 | 6.0756 | 0 | 0
2015-11-21 | 0 | 0 | 0.45 | 122.99 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 10.2124 | 6.3842 | 0 | 0
2015-11-22 | 0 | 0 | 0.45 | 122.54 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 10.521 | 6.6927 | 0 | 0
2015-11-23 | 0 | 0 | 0.45 | 122.09 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 10.8296 | 7.0013 | 0 | 0
2015-11-24 | 0 | 0 | 0.45 | 121.64 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 11.1382 | 7.3099 | 0 | 0
2015-11-25 | 0 | 0 | 0.45 | 121.19 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 11.4467 | 7.6185 | 0 | 0
2015-11-26 | 0 | 0 | 0.45 | 120.74 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 11.7553 | 7.927 | 0 | 0
2015-11-27 | 0 | 0 | 0.45 | 120.29 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 12.0639 | 8.2356 | 0 | 0
2015-11-28 | 0 | 0 | 0.45 | 119.84 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 12.3724 | 8.5442 | 0 | 0
2015-11-29 | 0 | 0 | 0.45 | 119.39 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 12.681 | 8.8527 | 0 | 0
2015-11-30 | 13 | 1.3 | 0.45 | 120.24 | 190000 | 343055.5556 | 0.34306 | 6500 | 6.5 | 13000000 | 13 | 1200 | 4.32 | 17.6631 | 1.2616 | 13.9427 | 10.1144 | 0 | 0
2015-12-01 | 34.6 | 2.5 | 0.45 | 122.29 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 16.0841 | 12.2558 | 0 | 0
2015-12-02 | 27.4 | 2.5 | 0.45 | 124.34 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 18.2255 | 14.3972 | 0 | 0
2015-12-03 | 32.6 | 2.5 | 0.45 | 126.39 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 20.3669 | 16.5386 | 0 | 0
2015-12-04 | 27.2 | 2.5 | 0.45 | 128.44 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 22.5083 | 18.68 | 0 | 0
2015-12-05 | 33.8 | 2.5 | 0.45 | 130.49 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 24.6497 | 20.8214 | 0 | 0
2015-12-06 | 22.4 | 2.24 | 0.45 | 132.28 | 190000 | 591111.1111 | 0.59111 | 11200 | 11.2 | 22400000 | 22.4 | 1200 | 4.32 | 27.3111 | 1.9508 | 26.6005 | 22.7722 | 0 | 0
2015-12-07 | 37.2 | 2.5 | 0.45 | 134.33 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 28.7419 | 24.9136 | 0 | 0
2015-12-08 | 27 | 2.5 | 0.45 | 136.38 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 30.8833 | 27.055 | 0 | 0
2015-12-09 | 4.8 | 0.48 | 0.45 | 136.41 | 190000 | 126666.6667 | 0.12667 | 2400 | 2.4 | 4800000 | 4.8 | 1200 | 4.32 | 9.2467 | 0.66048 | 31.5438 | 27.7155 | 0 | 0
2015-12-10 | 12.2 | 1.22 | 0.45 | 137.18 | 190000 | 321944.4444 | 0.32194 | 6100 | 6.1 | 12200000 | 12.2 | 1200 | 4.32 | 16.8419 | 1.203 | 32.7468 | 28.9185 | 0 | 0
2015-12-11 | 3.4 | 0.34 | 0.45 | 137.07 | 190000 | 89722.2222 | 0.089722 | 1700 | 1.7 | 3400000 | 3.4 | 1200 | 4.32 | 7.8097 | 0.55784 | 33.3046 | 29.4763 | 0 | 0
2015-12-12 | 23.8 | 2.38 | 0.45 | 139 | 190000 | 628055.5556 | 0.62806 | 11900 | 11.9 | 23800000 | 23.8 | 1200 | 4.32 | 28.7481 | 2.0534 | 35.3581 | 31.5298 | 0 | 0
2015-12-13 | 0 | 0 | 0.45 | 138.55 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 35.6666 | 31.8384 | 0 | 0
2015-12-14 | 2.4 | 0.24 | 0.45 | 138.34 | 190000 | 63333.3333 | 0.063333 | 1200 | 1.2 | 2400000 | 2.4 | 1200 | 4.32 | 6.7833 | 0.48452 | 36.1512 | 32.3229 | 0 | 0
2015-12-15 | 3 | 0.3 | 0.45 | 138.19 | 190000 | 79166.6667 | 0.079167 | 1500 | 1.5 | 3000000 | 3 | 1200 | 4.32 | 7.3992 | 0.52851 | 36.6797 | 32.8514 | 0 | 0
2015-12-16 | 2.2 | 0.22 | 0.45 | 137.96 | 190000 | 58055.5556 | 0.058056 | 1100 | 1.1 | 2200000 | 2.2 | 1200 | 4.32 | 6.5781 | 0.46986 | 37.1495 | 33.3212 | 0 | 0
2015-12-17 | 21.8 | 2.18 | 0.45 | 139.69 | 190000 | 575277.7778 | 0.57528 | 10900 | 10.9 | 21800000 | 21.8 | 1200 | 4.32 | 26.6953 | 1.9068 | 39.0563 | 35.2281 | 0 | 0
2015-12-18 | 25.5 | 2.5 | 0.45 | 141.74 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 41.1977 | 37.3695 | 0 | 0
2015-12-19 | 31.8 | 2.5 | 0.45 | 143.79 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 43.3391 | 39.5109 | 0 | 0
2015-12-20 | 22.6 | 2.26 | 0.45 | 145.6 | 190000 | 596388.8889 | 0.59639 | 11300 | 11.3 | 22600000 | 22.6 | 1200 | 4.32 | 27.5164 | 1.9655 | 45.3046 | 41.4763 | 0 | 0
2015-12-21 | 9 | 0.9 | 0.45 | 146.05 | 190000 | 237500 | 0.2375 | 4500 | 4.5 | 9000000 | 9 | 1200 | 4.32 | 13.5575 | 0.96839 | 46.273 | 42.4447 | 0 | 0
2015-12-22 | 35.8 | 2.5 | 0.45 | 148.1 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 48.4144 | 44.5861 | 0 | 0
2015-12-23 | 9.4 | 0.94 | 0.45 | 148.59 | 190000 | 248055.5556 | 0.24806 | 4700 | 4.7 | 9400000 | 9.4 | 1200 | 4.32 | 13.9681 | 0.99772 | 49.4121 | 45.5838 | 0 | 0
2015-12-24 | 0 | 0 | 0.45 | 148.14 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 49.7207 | 45.8924 | 0 | 0
2015-12-25 | 0 | 0 | 0.45 | 147.69 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 50.0293 | 46.201 | 0 | 0
2015-12-26 | 26.2 | 2.5 | 0.45 | 149.74 | 190000 | 659722.2222 | 0.65972 | 12500 | 12.5 | 25000000 | 25 | 1200 | 4.32 | 29.9797 | 2.1414 | 52.1707 | 48.3424 | 0 | 0
2015-12-27 | 1.6 | 0.16 | 0.45 | 149.45 | 190000 | 42222.2222 | 0.042222 | 800 | 0.8 | 1600000 | 1.6 | 1200 | 4.32 | 5.9622 | 0.42587 | 52.5965 | 48.7683 | 0 | 0
2015-12-28 | 0.2 | 0.02 | 0.45 | 149.02 | 190000 | 5277.7778 | 0.0052778 | 100 | 0.1 | 200000 | 0.2 | 1200 | 4.32 | 4.5253 | 0.32323 | 52.9198 | 49.0915 | 0 | 0
2015-12-29 | 0 | 0 | 0.45 | 148.57 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 53.2284 | 49.4001 | 0 | 0
2015-12-30 | 0 | 0 | 0.45 | 148.12 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 53.5369 | 49.7087 | 0 | 0
2015-12-31 | 0 | 0 | 0.45 | 147.67 | 190000 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 4.32 | 4.32 | 0.30857 | 53.8455 | 50.0172 | 0 | 0

## Solar
Number of Panels | 13 |  |  | Cost |  | Maintainance
Area of panels | 1.6 | m^2 |  | Panels | 6500 | Minumum | 50
Efficiency | 17% |  |  | Inverter | 2369 | Maximum | 375
GHG Emissions | 496 | kgCO2e |  | Batteries | 1950 | Solar Panels | 20 | 4/year
Maintainance | 4 | # per year |  |  | 10819 | Filters | 8
Intensity | 350 | W/m^2 |  |  |  | Total | 28
Batteries | 5
Inverter | [5 empty] | Satisfaction | 98.87%
Eff of Inverter | 92%
Eff of battery | 96% |  |  | CO2 Emissions | [kgCO2e]
Capacity of batteries | 36 | MJ |  | Panels | 6448
|  |  |  | Inverter | 100
Weather | Average Hours Sun |  |  | Batteries | 1200
January | 8.5 |  |  |  | 2408
February | 10 |  |  | Total | 10156
March | 11.8
April | 13.6 |  |  | Satisfaction | 70.44%
May | 15.3
June | 16
July | 15.8 |  |  | Shipping | 21185.6875
August | 14.2 |  |  | Maximum | 22244.9719
September | 12.5 |  |  | Minimum | 3177.8531
October | 10.8
November | 9
December | 8.3
Date | Power needed per day | Hours of sun | Energy into battery | Energy Out | Energy Remaining
[] | [MJ] | [h] | [MJ] | [MJ]
2014-01-01 | 19.2961 | 8.5 | 36 | 31.7952 | 12.4991
2014-01-02 | 20.3225 | 8.5 | 36 | 31.7952 | 11.4727
2014-01-03 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-04 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-05 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-06 | 5.1319 | 8.5 | 36 | 31.7952 | 26.6633
2014-01-07 | 20.9383 | 8.5 | 36 | 31.7952 | 10.8569
2014-01-08 | 25.4544 | 8.5 | 36 | 31.7952 | 6.3408
2014-01-09 | 25.6597 | 8.5 | 36 | 31.7952 | 6.1355
2014-01-10 | 25.6597 | 8.5 | 36 | 31.7952 | 6.1355
2014-01-11 | 14.78 | 8.5 | 36 | 31.7952 | 17.0152
2014-01-12 | 25.6597 | 8.5 | 36 | 31.7952 | 6.1355
2014-01-13 | 9.8533 | 8.5 | 36 | 31.7952 | 21.9419
2014-01-14 | 5.9531 | 8.5 | 36 | 31.7952 | 25.8421
2014-01-15 | 1.6422 | 8.5 | 36 | 31.7952 | 30.153
2014-01-16 | 0.82111 | 8.5 | 36 | 31.7952 | 30.9741
2014-01-17 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-18 | 2.6686 | 8.5 | 36 | 31.7952 | 29.1266
2014-01-19 | 1.0264 | 8.5 | 36 | 31.7952 | 30.7688
2014-01-20 | 0.61583 | 8.5 | 36 | 31.7952 | 31.1794
2014-01-21 | 0.82111 | 8.5 | 36 | 31.7952 | 30.9741
2014-01-22 | 0.61583 | 8.5 | 36 | 31.7952 | 31.1794
2014-01-23 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-24 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-25 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-26 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-27 | 18.0644 | 8.5 | 36 | 31.7952 | 13.7308
2014-01-28 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-29 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-30 | 0 | 8.5 | 36 | 31.7952 | 31.7952
2014-01-31 | 2.6686 | 8.5 | 36 | 31.7952 | 29.1266
2014-02-01 | 6.9886 | 10 | 36 | 31.7952 | 24.8066
2014-02-02 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-03 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-04 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-05 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-06 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-07 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-08 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-09 | 16.8419 | 10 | 36 | 31.7952 | 14.9533
2014-02-10 | 18.0736 | 10 | 36 | 31.7952 | 13.7216
2014-02-11 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2014-02-12 | 21.5633 | 10 | 36 | 31.7952 | 10.2319
2014-02-13 | 20.3317 | 10 | 36 | 31.7952 | 11.4635
2014-02-14 | 7.3992 | 10 | 36 | 31.7952 | 24.396
2014-02-15 | 16.2261 | 10 | 36 | 31.7952 | 15.5691
2014-02-16 | 23.8214 | 10 | 36 | 31.7952 | 7.9738
2014-02-17 | 13.7628 | 10 | 36 | 31.7952 | 18.0324
2014-02-18 | 17.2525 | 10 | 36 | 31.7952 | 14.5427
2014-02-19 | 26.6953 | 10 | 36 | 31.7952 | 5.0999
2014-02-20 | 6.7833 | 10 | 36 | 31.7952 | 25.0119
2014-02-21 | 5.1411 | 10 | 36 | 31.7952 | 26.6541
2014-02-22 | 9.2467 | 10 | 36 | 31.7952 | 22.5485
2014-02-23 | 19.3053 | 10 | 36 | 31.7952 | 12.4899
2014-02-24 | 11.2994 | 10 | 36 | 31.7952 | 20.4958
2014-02-25 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-26 | 5.1411 | 10 | 36 | 31.7952 | 26.6541
2014-02-27 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2014-02-28 | 4.7306 | 10 | 36 | 31.7952 | 27.0646
2014-03-01 | 6.3728 | 11.8 | 36 | 31.7952 | 25.4224
2014-03-02 | 23.8214 | 11.8 | 36 | 31.7952 | 7.9738
2014-03-03 | 5.3464 | 11.8 | 36 | 31.7952 | 26.4488
2014-03-04 | 6.7833 | 11.8 | 36 | 31.7952 | 25.0119
2014-03-05 | 28.7481 | 11.8 | 36 | 31.7952 | 3.0471
2014-03-06 | 13.1469 | 11.8 | 36 | 31.7952 | 18.6483
2014-03-07 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2014-03-08 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2014-03-09 | 15.1997 | 11.8 | 36 | 31.7952 | 16.5955
2014-03-10 | 6.7833 | 11.8 | 36 | 31.7952 | 25.0119
2014-03-11 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2014-03-12 | 7.1939 | 11.8 | 36 | 31.7952 | 24.6013
2014-03-13 | 25.0531 | 11.8 | 36 | 31.7952 | 6.7421
2014-03-14 | 18.4842 | 11.8 | 36 | 31.7952 | 13.311
2014-03-15 | 27.7217 | 11.8 | 36 | 31.7952 | 4.0735
2014-03-16 | 9.8625 | 11.8 | 36 | 31.7952 | 21.9327
2014-03-17 | 4.7306 | 11.8 | 36 | 31.7952 | 27.0646
2014-03-18 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2014-03-19 | 5.9622 | 11.8 | 36 | 31.7952 | 25.833
2014-03-20 | 5.9622 | 11.8 | 36 | 31.7952 | 25.833
2014-03-21 | 12.1206 | 11.8 | 36 | 31.7952 | 19.6746
2014-03-22 | 6.9886 | 11.8 | 36 | 31.7952 | 24.8066
2014-03-23 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2014-03-24 | 8.4256 | 11.8 | 36 | 31.7952 | 23.3696
2014-03-25 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2014-03-26 | 4.5253 | 11.8 | 36 | 31.7952 | 27.2699
2014-03-27 | 8.8361 | 11.8 | 36 | 31.7952 | 22.9591
2014-03-28 | 28.5428 | 11.8 | 36 | 31.7952 | 3.2524
2014-03-29 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2014-03-30 | 7.3992 | 11.8 | 36 | 31.7952 | 24.396
2014-03-31 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2014-04-01 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-04-02 | 10.0678 | 13.6 | 36 | 31.7952 | 21.7274
2014-04-03 | 25.2583 | 13.6 | 36 | 31.7952 | 6.5369
2014-04-04 | 6.9886 | 13.6 | 36 | 31.7952 | 24.8066
2014-04-05 | 20.6396 | 13.6 | 36 | 31.7952 | 11.1556
2014-04-06 | 13.9681 | 13.6 | 36 | 31.7952 | 17.8271
2014-04-07 | 18.2789 | 13.6 | 36 | 31.7952 | 13.5163
2014-04-08 | 10.0678 | 13.6 | 36 | 31.7952 | 21.7274
2014-04-09 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-04-10 | 21.3581 | 13.6 | 36 | 31.7952 | 10.4371
2014-04-11 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-04-12 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-04-13 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-04-14 | 19.5106 | 13.6 | 36 | 31.7952 | 12.2846
2014-04-15 | 25.6689 | 13.6 | 36 | 31.7952 | 6.1263
2014-04-16 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2014-04-17 | 14.3786 | 13.6 | 36 | 31.7952 | 17.4166
2014-04-18 | 6.2701 | 13.6 | 36 | 31.7952 | 25.5251
2014-04-19 | 25.8742 | 13.6 | 36 | 31.7952 | 5.921
2014-04-20 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2014-04-21 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-04-22 | 8.8361 | 13.6 | 36 | 31.7952 | 22.9591
2014-04-23 | 17.4578 | 13.6 | 36 | 31.7952 | 14.3374
2014-04-24 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2014-04-25 | 6.1675 | 13.6 | 36 | 31.7952 | 25.6277
2014-04-26 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2014-04-27 | 11.71 | 13.6 | 36 | 31.7952 | 20.0852
2014-04-28 | 5.1411 | 13.6 | 36 | 31.7952 | 26.6541
2014-04-29 | 4.4226 | 13.6 | 36 | 31.7952 | 27.3726
2014-04-30 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2014-05-01 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-02 | 6.3728 | 15.3 | 36 | 31.7952 | 25.4224
2014-05-03 | 9.0414 | 15.3 | 36 | 31.7952 | 22.7538
2014-05-04 | 8.2203 | 15.3 | 36 | 31.7952 | 23.5749
2014-05-05 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-06 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-07 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-08 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-09 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-10 | 4.5253 | 15.3 | 36 | 31.7952 | 27.2699
2014-05-11 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-12 | 4.5253 | 15.3 | 36 | 31.7952 | 27.2699
2014-05-13 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-14 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-15 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-16 | 7.1939 | 15.3 | 36 | 31.7952 | 24.6013
2014-05-17 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-18 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-19 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-20 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-21 | 12.7364 | 15.3 | 36 | 31.7952 | 19.0588
2014-05-22 | 29.9797 | 15.3 | 36 | 31.7952 | 1.8155
2014-05-23 | 5.1411 | 15.3 | 36 | 31.7952 | 26.6541
2014-05-24 | 9.6572 | 15.3 | 36 | 31.7952 | 22.138
2014-05-25 | 28.3375 | 15.3 | 36 | 31.7952 | 3.4577
2014-05-26 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-27 | 8.8361 | 15.3 | 36 | 31.7952 | 22.9591
2014-05-28 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-29 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-30 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-05-31 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2014-06-01 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-02 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-03 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-04 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-05 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-06 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-07 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-08 | 4.5253 | 16 | 36 | 31.7952 | 27.2699
2014-06-09 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-10 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-11 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-12 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-13 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-14 | 8.015 | 16 | 36 | 31.7952 | 23.7802
2014-06-15 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-16 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-17 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-18 | 5.9622 | 16 | 36 | 31.7952 | 25.833
2014-06-19 | 25.6689 | 16 | 36 | 31.7952 | 6.1263
2014-06-20 | 7.6044 | 16 | 36 | 31.7952 | 24.1908
2014-06-21 | 5.5517 | 16 | 36 | 31.7952 | 26.2435
2014-06-22 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-23 | 20.1264 | 16 | 36 | 31.7952 | 11.6688
2014-06-24 | 5.5517 | 16 | 36 | 31.7952 | 26.2435
2014-06-25 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-06-26 | 10.2731 | 16 | 36 | 31.7952 | 21.5221
2014-06-27 | 25.2583 | 16 | 36 | 31.7952 | 6.5369
2014-06-28 | 25.2583 | 16 | 36 | 31.7952 | 6.5369
2014-06-29 | 4.9358 | 16 | 36 | 31.7952 | 26.8594
2014-06-30 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2014-07-01 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-02 | 6.1675 | 15.8 | 36 | 31.7952 | 25.6277
2014-07-03 | 10.6836 | 15.8 | 36 | 31.7952 | 21.1116
2014-07-04 | 13.9681 | 15.8 | 36 | 31.7952 | 17.8271
2014-07-05 | 29.9797 | 15.8 | 36 | 31.7952 | 1.8155
2014-07-06 | 18.2789 | 15.8 | 36 | 31.7952 | 13.5163
2014-07-07 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-08 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-09 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-10 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-11 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-12 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-13 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-14 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-15 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-16 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-17 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-18 | 29.9797 | 15.8 | 36 | 31.7952 | 1.8155
2014-07-19 | 6.1675 | 15.8 | 36 | 31.7952 | 25.6277
2014-07-20 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-21 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-22 | 12.5311 | 15.8 | 36 | 31.7952 | 19.2641
2014-07-23 | 23.0003 | 15.8 | 36 | 31.7952 | 8.7949
2014-07-24 | 4.9358 | 15.8 | 36 | 31.7952 | 26.8594
2014-07-25 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-26 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-27 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-28 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-29 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-30 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-07-31 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2014-08-01 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-02 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-03 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-04 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-05 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-06 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-07 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-08 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-09 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-10 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-11 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-12 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-13 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-14 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-15 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-16 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-17 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-18 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-19 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-20 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-21 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-22 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-23 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-24 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-25 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-26 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-27 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2014-08-28 | 4.7306 | 14.2 | 36 | 31.7952 | 27.0646
2014-08-29 | 12.3258 | 14.2 | 36 | 31.7952 | 19.4694
2014-08-30 | 8.015 | 14.2 | 36 | 31.7952 | 23.7802
2014-08-31 | 15.1997 | 14.2 | 36 | 31.7952 | 16.5955
2014-09-01 | 7.6044 | 12.5 | 36 | 31.7952 | 24.1908
2014-09-02 | 10.6836 | 12.5 | 36 | 31.7952 | 21.1116
2014-09-03 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-04 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-05 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-06 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-07 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-08 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-09 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-10 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-11 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-12 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-13 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-14 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-15 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-16 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-17 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-18 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2014-09-19 | 4.7306 | 12.5 | 36 | 31.7952 | 27.0646
2014-09-20 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-21 | 6.3728 | 12.5 | 36 | 31.7952 | 25.4224
2014-09-22 | 17.0472 | 12.5 | 36 | 31.7952 | 14.748
2014-09-23 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2014-09-24 | 5.9622 | 12.5 | 36 | 31.7952 | 25.833
2014-09-25 | 4.9358 | 12.5 | 36 | 31.7952 | 26.8594
2014-09-26 | 12.7364 | 12.5 | 36 | 31.7952 | 19.0588
2014-09-27 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-09-28 | 17.0472 | 12.5 | 36 | 31.7952 | 14.748
2014-09-29 | 10.0678 | 12.5 | 36 | 31.7952 | 21.7274
2014-09-30 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2014-10-01 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2014-10-02 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2014-10-03 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-04 | 10.4783 | 10.8 | 36 | 31.7952 | 21.3169
2014-10-05 | 13.7628 | 10.8 | 36 | 31.7952 | 18.0324
2014-10-06 | 4.7306 | 10.8 | 36 | 31.7952 | 27.0646
2014-10-07 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2014-10-08 | 5.7569 | 10.8 | 36 | 31.7952 | 26.0383
2014-10-09 | 6.1675 | 10.8 | 36 | 31.7952 | 25.6277
2014-10-10 | 22.5897 | 10.8 | 36 | 31.7952 | 9.2055
2014-10-11 | 20.1264 | 10.8 | 36 | 31.7952 | 11.6688
2014-10-12 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-13 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-14 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-15 | 10.8889 | 10.8 | 36 | 31.7952 | 20.9063
2014-10-16 | 21.9739 | 10.8 | 36 | 31.7952 | 9.8213
2014-10-17 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-18 | 21.5633 | 10.8 | 36 | 31.7952 | 10.2319
2014-10-19 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-20 | 15.405 | 10.8 | 36 | 31.7952 | 16.3902
2014-10-21 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-22 | 26.2847 | 10.8 | 36 | 31.7952 | 5.5105
2014-10-23 | 13.9681 | 10.8 | 36 | 31.7952 | 17.8271
2014-10-24 | 5.9622 | 10.8 | 36 | 31.7952 | 25.833
2014-10-25 | 26.6953 | 10.8 | 36 | 31.7952 | 5.0999
2014-10-26 | 6.7833 | 10.8 | 36 | 31.7952 | 25.0119
2014-10-27 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2014-10-28 | 29.3639 | 10.8 | 36 | 31.7952 | 2.4313
2014-10-29 | 11.5047 | 10.8 | 36 | 31.7952 | 20.2905
2014-10-30 | 13.5575 | 10.8 | 36 | 31.7952 | 18.2377
2014-10-31 | 19.7158 | 10.8 | 36 | 31.7952 | 12.0794
2014-11-01 | 10.8889 | 9 | 36 | 31.7952 | 20.9063
2014-11-02 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-03 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-04 | 13.5575 | 9 | 36 | 31.7952 | 18.2377
2014-11-05 | 8.8361 | 9 | 36 | 31.7952 | 22.9591
2014-11-06 | 25.0531 | 9 | 36 | 31.7952 | 6.7421
2014-11-07 | 5.7569 | 9 | 36 | 31.7952 | 26.0383
2014-11-08 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-09 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-10 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-11 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-12 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-13 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-14 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-15 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-16 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-17 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-18 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-19 | 7.8097 | 9 | 36 | 31.7952 | 23.9855
2014-11-20 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-21 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-22 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-23 | 19.9211 | 9 | 36 | 31.7952 | 11.8741
2014-11-24 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-25 | 19.7158 | 9 | 36 | 31.7952 | 12.0794
2014-11-26 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2014-11-27 | 19.7158 | 9 | 36 | 31.7952 | 12.0794
2014-11-28 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-29 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-11-30 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2014-12-01 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-02 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-03 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-04 | 5.5517 | 8.3 | 35.5003 | 31.3539 | 25.8022
2014-12-05 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2014-12-06 | 5.1411 | 8.3 | 35.5003 | 31.3539 | 26.2128
2014-12-07 | 19.9211 | 8.3 | 35.5003 | 31.3539 | 11.4328
2014-12-08 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2014-12-09 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2014-12-10 | 8.8361 | 8.3 | 35.5003 | 31.3539 | 22.5178
2014-12-11 | 22.5897 | 8.3 | 35.5003 | 31.3539 | 8.7642
2014-12-12 | 5.7569 | 8.3 | 35.5003 | 31.3539 | 25.5969
2014-12-13 | 5.3464 | 8.3 | 35.5003 | 31.3539 | 26.0075
2014-12-14 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-15 | 13.5575 | 8.3 | 35.5003 | 31.3539 | 17.7964
2014-12-16 | 25.0531 | 8.3 | 35.5003 | 31.3539 | 6.3008
2014-12-17 | 5.1411 | 8.3 | 35.5003 | 31.3539 | 26.2128
2014-12-18 | 29.5692 | 8.3 | 35.5003 | 31.3539 | 1.7847
2014-12-19 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-20 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-21 | 13.3522 | 8.3 | 35.5003 | 31.3539 | 18.0017
2014-12-22 | 16.2261 | 8.3 | 35.5003 | 31.3539 | 15.1278
2014-12-23 | 14.5839 | 8.3 | 35.5003 | 31.3539 | 16.77
2014-12-24 | 6.5781 | 8.3 | 35.5003 | 31.3539 | 24.7758
2014-12-25 | 4.9358 | 8.3 | 35.5003 | 31.3539 | 26.418
2014-12-26 | 14.7892 | 8.3 | 35.5003 | 31.3539 | 16.5647
2014-12-27 | 9.8625 | 8.3 | 35.5003 | 31.3539 | 21.4914
2014-12-28 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-29 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-30 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2014-12-31 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2015-01-01 | 12.3258 | 8.5 | 36 | 31.7952 | 19.4694
2015-01-02 | 5.3464 | 8.5 | 36 | 31.7952 | 26.4488
2015-01-03 | 18.0736 | 8.5 | 36 | 31.7952 | 13.7216
2015-01-04 | 29.9797 | 8.5 | 36 | 31.7952 | 1.8155
2015-01-05 | 29.9797 | 8.5 | 36 | 31.7952 | 1.8155
2015-01-06 | 7.1939 | 8.5 | 36 | 31.7952 | 24.6013
2015-01-07 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-08 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-09 | 5.1411 | 8.5 | 36 | 31.7952 | 26.6541
2015-01-10 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-11 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-12 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-13 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-14 | 4.7306 | 8.5 | 36 | 31.7952 | 27.0646
2015-01-15 | 29.9797 | 8.5 | 36 | 31.7952 | 1.8155
2015-01-16 | 10.4783 | 8.5 | 36 | 31.7952 | 21.3169
2015-01-17 | 25.2583 | 8.5 | 36 | 31.7952 | 6.5369
2015-01-18 | 21.3581 | 8.5 | 36 | 31.7952 | 10.4371
2015-01-19 | 6.9886 | 8.5 | 36 | 31.7952 | 24.8066
2015-01-20 | 4.7306 | 8.5 | 36 | 31.7952 | 27.0646
2015-01-21 | 23.2056 | 8.5 | 36 | 31.7952 | 8.5896
2015-01-22 | 18.6894 | 8.5 | 36 | 31.7952 | 13.1058
2015-01-23 | 29.9797 | 8.5 | 36 | 31.7952 | 1.8155
2015-01-24 | 29.9797 | 8.5 | 36 | 31.7952 | 1.8155
2015-01-25 | 6.1675 | 8.5 | 36 | 31.7952 | 25.6277
2015-01-26 | 7.1939 | 8.5 | 36 | 31.7952 | 24.6013
2015-01-27 | 7.1939 | 8.5 | 36 | 31.7952 | 24.6013
2015-01-28 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-29 | 4.32 | 8.5 | 36 | 31.7952 | 27.4752
2015-01-30 | 4.9358 | 8.5 | 36 | 31.7952 | 26.8594
2015-01-31 | 10.2731 | 8.5 | 36 | 31.7952 | 21.5221
2015-02-01 | 12.5311 | 10 | 36 | 31.7952 | 19.2641
2015-02-02 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2015-02-03 | 4.9358 | 10 | 36 | 31.7952 | 26.8594
2015-02-04 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2015-02-05 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2015-02-06 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2015-02-07 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2015-02-08 | 11.0942 | 10 | 36 | 31.7952 | 20.701
2015-02-09 | 7.6044 | 10 | 36 | 31.7952 | 24.1908
2015-02-10 | 4.5253 | 10 | 36 | 31.7952 | 27.2699
2015-02-11 | 24.4372 | 10 | 36 | 31.7952 | 7.358
2015-02-12 | 29.9797 | 10 | 36 | 31.7952 | 1.8155
2015-02-13 | 23.8214 | 10 | 36 | 31.7952 | 7.9738
2015-02-14 | 4.5253 | 10 | 36 | 31.7952 | 27.2699
2015-02-15 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-02-16 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-02-17 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-02-18 | 8.4256 | 10 | 36 | 31.7952 | 23.3696
2015-02-19 | 15.6103 | 10 | 36 | 31.7952 | 16.1849
2015-02-20 | 4.7306 | 10 | 36 | 31.7952 | 27.0646
2015-02-21 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-02-22 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-02-23 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-02-24 | 4.5253 | 10 | 36 | 31.7952 | 27.2699
2015-02-25 | 9.0414 | 10 | 36 | 31.7952 | 22.7538
2015-02-26 | 13.3522 | 10 | 36 | 31.7952 | 18.443
2015-02-27 | 4.7306 | 10 | 36 | 31.7952 | 27.0646
2015-02-28 | 4.32 | 10 | 36 | 31.7952 | 27.4752
2015-03-01 | 5.5517 | 11.8 | 36 | 31.7952 | 26.2435
2015-03-02 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-03 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-04 | 4.7306 | 11.8 | 36 | 31.7952 | 27.0646
2015-03-05 | 6.1675 | 11.8 | 36 | 31.7952 | 25.6277
2015-03-06 | 5.1411 | 11.8 | 36 | 31.7952 | 26.6541
2015-03-07 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-08 | 4.7306 | 11.8 | 36 | 31.7952 | 27.0646
2015-03-09 | 4.7306 | 11.8 | 36 | 31.7952 | 27.0646
2015-03-10 | 7.1939 | 11.8 | 36 | 31.7952 | 24.6013
2015-03-11 | 18.2789 | 11.8 | 36 | 31.7952 | 13.5163
2015-03-12 | 13.1469 | 11.8 | 36 | 31.7952 | 18.6483
2015-03-13 | 22.1792 | 11.8 | 36 | 31.7952 | 9.616
2015-03-14 | 4.9358 | 11.8 | 36 | 31.7952 | 26.8594
2015-03-15 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-16 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-17 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-18 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-19 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-20 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-21 | 4.32 | 11.8 | 36 | 31.7952 | 27.4752
2015-03-22 | 11.5047 | 11.8 | 36 | 31.7952 | 20.2905
2015-03-23 | 14.1733 | 11.8 | 36 | 31.7952 | 17.6219
2015-03-24 | 23.0003 | 11.8 | 36 | 31.7952 | 8.7949
2015-03-25 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-26 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-27 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-28 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-29 | 14.5839 | 11.8 | 36 | 31.7952 | 17.2113
2015-03-30 | 29.9797 | 11.8 | 36 | 31.7952 | 1.8155
2015-03-31 | 16.2261 | 11.8 | 36 | 31.7952 | 15.5691
2015-04-01 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-02 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2015-04-03 | 13.5575 | 13.6 | 36 | 31.7952 | 18.2377
2015-04-04 | 12.9417 | 13.6 | 36 | 31.7952 | 18.8535
2015-04-05 | 4.9358 | 13.6 | 36 | 31.7952 | 26.8594
2015-04-06 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-07 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-08 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-09 | 7.6044 | 13.6 | 36 | 31.7952 | 24.1908
2015-04-10 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2015-04-11 | 13.7628 | 13.6 | 36 | 31.7952 | 18.0324
2015-04-12 | 29.3639 | 13.6 | 36 | 31.7952 | 2.4313
2015-04-13 | 20.9475 | 13.6 | 36 | 31.7952 | 10.8477
2015-04-14 | 5.8596 | 13.6 | 36 | 31.7952 | 25.9356
2015-04-15 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2015-04-16 | 7.3992 | 13.6 | 36 | 31.7952 | 24.396
2015-04-17 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-18 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-19 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-20 | 5.449 | 13.6 | 36 | 31.7952 | 26.3462
2015-04-21 | 4.7306 | 13.6 | 36 | 31.7952 | 27.0646
2015-04-22 | 12.7364 | 13.6 | 36 | 31.7952 | 19.0588
2015-04-23 | 12.9417 | 13.6 | 36 | 31.7952 | 18.8535
2015-04-24 | 6.1675 | 13.6 | 36 | 31.7952 | 25.6277
2015-04-25 | 4.32 | 13.6 | 36 | 31.7952 | 27.4752
2015-04-26 | 8.6308 | 13.6 | 36 | 31.7952 | 23.1644
2015-04-27 | 27.3111 | 13.6 | 36 | 31.7952 | 4.4841
2015-04-28 | 20.1264 | 13.6 | 36 | 31.7952 | 11.6688
2015-04-29 | 29.9797 | 13.6 | 36 | 31.7952 | 1.8155
2015-04-30 | 9.2467 | 13.6 | 36 | 31.7952 | 22.5485
2015-05-01 | 5.1411 | 15.3 | 36 | 31.7952 | 26.6541
2015-05-02 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-03 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-04 | 24.6425 | 15.3 | 36 | 31.7952 | 7.1527
2015-05-05 | 4.7306 | 15.3 | 36 | 31.7952 | 27.0646
2015-05-06 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-07 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-08 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-09 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-10 | 4.7306 | 15.3 | 36 | 31.7952 | 27.0646
2015-05-11 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-12 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-13 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-14 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-15 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-16 | 4.5253 | 15.3 | 36 | 31.7952 | 27.2699
2015-05-17 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-18 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-19 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-20 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-21 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-22 | 4.5253 | 15.3 | 36 | 31.7952 | 27.2699
2015-05-23 | 4.5253 | 15.3 | 36 | 31.7952 | 27.2699
2015-05-24 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-25 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-26 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-27 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-28 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-29 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-30 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-05-31 | 4.32 | 15.3 | 36 | 31.7952 | 27.4752
2015-06-01 | 11.9153 | 16 | 36 | 31.7952 | 19.8799
2015-06-02 | 7.1939 | 16 | 36 | 31.7952 | 24.6013
2015-06-03 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-04 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-05 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-06 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-07 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-08 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-09 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-10 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-11 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-12 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-13 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-14 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-15 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-16 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-17 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-18 | 11.5047 | 16 | 36 | 31.7952 | 20.2905
2015-06-19 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-20 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-21 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-22 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-23 | 5.7569 | 16 | 36 | 31.7952 | 26.0383
2015-06-24 | 18.0736 | 16 | 36 | 31.7952 | 13.7216
2015-06-25 | 8.4256 | 16 | 36 | 31.7952 | 23.3696
2015-06-26 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-27 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-28 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-29 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-06-30 | 4.32 | 16 | 36 | 31.7952 | 27.4752
2015-07-01 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-02 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-03 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-04 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-05 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-06 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-07 | 4.5253 | 15.8 | 36 | 31.7952 | 27.2699
2015-07-08 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-09 | 5.3464 | 15.8 | 36 | 31.7952 | 26.4488
2015-07-10 | 5.5517 | 15.8 | 36 | 31.7952 | 26.2435
2015-07-11 | 6.7833 | 15.8 | 36 | 31.7952 | 25.0119
2015-07-12 | 8.4256 | 15.8 | 36 | 31.7952 | 23.3696
2015-07-13 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-14 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-15 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-16 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-17 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-18 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-19 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-20 | 4.9358 | 15.8 | 36 | 31.7952 | 26.8594
2015-07-21 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-22 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-23 | 12.9417 | 15.8 | 36 | 31.7952 | 18.8535
2015-07-24 | 8.4256 | 15.8 | 36 | 31.7952 | 23.3696
2015-07-25 | 8.6308 | 15.8 | 36 | 31.7952 | 23.1644
2015-07-26 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-27 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-28 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-29 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-30 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-07-31 | 4.32 | 15.8 | 36 | 31.7952 | 27.4752
2015-08-01 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-02 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-03 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-04 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-05 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-06 | 7.6044 | 14.2 | 36 | 31.7952 | 24.1908
2015-08-07 | 19.3053 | 14.2 | 36 | 31.7952 | 12.4899
2015-08-08 | 29.3639 | 14.2 | 36 | 31.7952 | 2.4313
2015-08-09 | 6.1675 | 14.2 | 36 | 31.7952 | 25.6277
2015-08-10 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-11 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-12 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-13 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-14 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-15 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-16 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-17 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-18 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-19 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-20 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-21 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-22 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-23 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-24 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-25 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-26 | 4.32 | 14.2 | 36 | 31.7952 | 27.4752
2015-08-27 | 7.1939 | 14.2 | 36 | 31.7952 | 24.6013
2015-08-28 | 14.9944 | 14.2 | 36 | 31.7952 | 16.8008
2015-08-29 | 29.9797 | 14.2 | 36 | 31.7952 | 1.8155
2015-08-30 | 29.9797 | 14.2 | 36 | 31.7952 | 1.8155
2015-08-31 | 10.4783 | 14.2 | 36 | 31.7952 | 21.3169
2015-09-01 | 20.5369 | 12.5 | 36 | 31.7952 | 11.2583
2015-09-02 | 5.1411 | 12.5 | 36 | 31.7952 | 26.6541
2015-09-03 | 6.7833 | 12.5 | 36 | 31.7952 | 25.0119
2015-09-04 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-05 | 5.9622 | 12.5 | 36 | 31.7952 | 25.833
2015-09-06 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-07 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2015-09-08 | 17.6631 | 12.5 | 36 | 31.7952 | 14.1321
2015-09-09 | 5.7569 | 12.5 | 36 | 31.7952 | 26.0383
2015-09-10 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-11 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-12 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-13 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-14 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-15 | 6.3728 | 12.5 | 36 | 31.7952 | 25.4224
2015-09-16 | 8.4256 | 12.5 | 36 | 31.7952 | 23.3696
2015-09-17 | 7.1939 | 12.5 | 36 | 31.7952 | 24.6013
2015-09-18 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2015-09-19 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2015-09-20 | 5.7569 | 12.5 | 36 | 31.7952 | 26.0383
2015-09-21 | 8.6308 | 12.5 | 36 | 31.7952 | 23.1644
2015-09-22 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2015-09-23 | 29.9797 | 12.5 | 36 | 31.7952 | 1.8155
2015-09-24 | 16.4314 | 12.5 | 36 | 31.7952 | 15.3638
2015-09-25 | 5.9622 | 12.5 | 36 | 31.7952 | 25.833
2015-09-26 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-27 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-28 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-29 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-09-30 | 4.32 | 12.5 | 36 | 31.7952 | 27.4752
2015-10-01 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-02 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-03 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-04 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-05 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-06 | 8.4256 | 10.8 | 36 | 31.7952 | 23.3696
2015-10-07 | 20.3317 | 10.8 | 36 | 31.7952 | 11.4635
2015-10-08 | 13.7628 | 10.8 | 36 | 31.7952 | 18.0324
2015-10-09 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2015-10-10 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2015-10-11 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2015-10-12 | 5.1411 | 10.8 | 36 | 31.7952 | 26.6541
2015-10-13 | 4.9358 | 10.8 | 36 | 31.7952 | 26.8594
2015-10-14 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-15 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-16 | 18.8947 | 10.8 | 36 | 31.7952 | 12.9005
2015-10-17 | 10.8889 | 10.8 | 36 | 31.7952 | 20.9063
2015-10-18 | 28.3375 | 10.8 | 36 | 31.7952 | 3.4577
2015-10-19 | 4.9358 | 10.8 | 36 | 31.7952 | 26.8594
2015-10-20 | 14.7892 | 10.8 | 36 | 31.7952 | 17.006
2015-10-21 | 8.4256 | 10.8 | 36 | 31.7952 | 23.3696
2015-10-22 | 14.3786 | 10.8 | 36 | 31.7952 | 17.4166
2015-10-23 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-24 | 10.2731 | 10.8 | 36 | 31.7952 | 21.5221
2015-10-25 | 8.4256 | 10.8 | 36 | 31.7952 | 23.3696
2015-10-26 | 4.32 | 10.8 | 36 | 31.7952 | 27.4752
2015-10-27 | 11.2994 | 10.8 | 36 | 31.7952 | 20.4958
2015-10-28 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2015-10-29 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2015-10-30 | 29.9797 | 10.8 | 36 | 31.7952 | 1.8155
2015-10-31 | 26.0794 | 10.8 | 36 | 31.7952 | 5.7158
2015-11-01 | 5.5517 | 9 | 36 | 31.7952 | 26.2435
2015-11-02 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-03 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-04 | 7.8097 | 9 | 36 | 31.7952 | 23.9855
2015-11-05 | 10.4783 | 9 | 36 | 31.7952 | 21.3169
2015-11-06 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2015-11-07 | 6.5781 | 9 | 36 | 31.7952 | 25.2171
2015-11-08 | 5.9622 | 9 | 36 | 31.7952 | 25.833
2015-11-09 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-10 | 25.361 | 9 | 36 | 31.7952 | 6.4342
2015-11-11 | 23.6161 | 9 | 36 | 31.7952 | 8.1791
2015-11-12 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2015-11-13 | 16.0208 | 9 | 36 | 31.7952 | 15.7744
2015-11-14 | 4.9358 | 9 | 36 | 31.7952 | 26.8594
2015-11-15 | 10.4783 | 9 | 36 | 31.7952 | 21.3169
2015-11-16 | 29.9797 | 9 | 36 | 31.7952 | 1.8155
2015-11-17 | 10.6836 | 9 | 36 | 31.7952 | 21.1116
2015-11-18 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-19 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-20 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-21 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-22 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-23 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-24 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-25 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-26 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-27 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-28 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-29 | 4.32 | 9 | 36 | 31.7952 | 27.4752
2015-11-30 | 17.6631 | 9 | 36 | 31.7952 | 14.1321
2015-12-01 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-02 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-03 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-04 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-05 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-06 | 27.3111 | 8.3 | 35.5003 | 31.3539 | 4.0428
2015-12-07 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-08 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-09 | 9.2467 | 8.3 | 35.5003 | 31.3539 | 22.1072
2015-12-10 | 16.8419 | 8.3 | 35.5003 | 31.3539 | 14.5119
2015-12-11 | 7.8097 | 8.3 | 35.5003 | 31.3539 | 23.5442
2015-12-12 | 28.7481 | 8.3 | 35.5003 | 31.3539 | 2.6058
2015-12-13 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2015-12-14 | 6.7833 | 8.3 | 35.5003 | 31.3539 | 24.5705
2015-12-15 | 7.3992 | 8.3 | 35.5003 | 31.3539 | 23.9547
2015-12-16 | 6.5781 | 8.3 | 35.5003 | 31.3539 | 24.7758
2015-12-17 | 26.6953 | 8.3 | 35.5003 | 31.3539 | 4.6586
2015-12-18 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-19 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-20 | 27.5164 | 8.3 | 35.5003 | 31.3539 | 3.8375
2015-12-21 | 13.5575 | 8.3 | 35.5003 | 31.3539 | 17.7964
2015-12-22 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-23 | 13.9681 | 8.3 | 35.5003 | 31.3539 | 17.3858
2015-12-24 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2015-12-25 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2015-12-26 | 29.9797 | 8.3 | 35.5003 | 31.3539 | 1.3742
2015-12-27 | 5.9622 | 8.3 | 35.5003 | 31.3539 | 25.3917
2015-12-28 | 4.5253 | 8.3 | 35.5003 | 31.3539 | 26.8286
2015-12-29 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2015-12-30 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339
2015-12-31 | 4.32 | 8.3 | 35.5003 | 31.3539 | 27.0339

## Filters
Maintainance Calculation
Parameters | Storage Tank Height |  | h | 7.5 | m
| Distance to storage tank |  | L | 13.6015 | m
| Pipe Diameter |  | D | 0.02 | m
| Pipe Area |  | A | 0.00031416 | m^2
| Pipe Friction Factor |  | f | 0.05
| Loss Coeffiecent |  | K | 10
| Pressure from Storage |  | rho g h | 73575 | Pa
| Consumption |  | C | 450 | L/day
| Min Maintainance |  | M_min | 50 | #/5 years
| Max Maintainance |  | M_max | 375 | #/5 years
| Cf Value |  |  | 0.25447
| Min Flow Rate |  | Q_min | 15 | L/min
| Max Flow Rate |  | Q_max | 40 | L/min
Filter Moduluses |  |  | Cf | Actual Filter | Filter Life Data [L]
| Filter Size | Present? | [Pa/(m/s))] | Life [L] | No pre-filter | 5 µm pre | 200 µm pre
| 1 µm Filter | y | 10000 | 20000 | 5000 | 20000 | 15000
| 5 µm Filter | y | 4000 | 20000 | 10000 |  | 20000
| 200 µm Filter | y | 800 | 20000 | 20000
| Total |  | 14800
velocity | Q | Pressure in tank | Pressure Loss |  | Attributes |  |  | Weights | Satisfaction
[m/s] | [L/min] | [Pa] | [Pa] |  | Q_D | 28.9 | L/min | 15% | S(Q_D) | 58.75%
0 | 0 | 73575 | 0 |  | M | 37.5 | #/year | 15% | S(M) | 99.64%
0.025 | 0.47124 | 73575 | 383.7448 |  | C | 450 | L/day | 20% | S(C) | 65.18%
0.05 | 0.94248 | 73575 | 794.9919 | [5 empty] | Total | 36.79%
0.075 | 1.4137 | 73575 | 1233.7413
0.1 | 1.885 | 73575 | 1699.9929 |  |  | Total Volume Through Filter [L] |  |  | Maintainance for Filter Change |  |  | Day with | Cost
0.125 | 2.3562 | 73575 | 2193.7469 |  | Day | 1 µm Filter | 5 µm Filter | 200 µm Filter | 1 µm Filter | 5 µm Filter | 200 µm Filter | Operation | 1480
0.15 | 2.8274 | 73575 | 2715.0032 |  | 1 | 450 | 450 | 450
0.175 | 3.2987 | 73575 | 3263.7618 |  | 2 | 900 | 900 | 900 | 0 | 0 | 0
0.2 | 3.7699 | 73575 | 3840.0226 |  | 3 | 1350 | 1350 | 1350 | 0 | 0 | 0
0.225 | 4.2412 | 73575 | 4443.7858 |  | 4 | 1800 | 1800 | 1800 | 0 | 0 | 0
0.25 | 4.7124 | 73575 | 5075.0513 |  | 5 | 2250 | 2250 | 2250 | 0 | 0 | 0
0.275 | 5.1836 | 73575 | 5733.819 |  | 6 | 2700 | 2700 | 2700 | 0 | 0 | 0
0.3 | 5.6549 | 73575 | 6420.0891 |  | 7 | 3150 | 3150 | 3150 | 0 | 0 | 0
0.325 | 6.1261 | 73575 | 7133.8615 |  | 8 | 3600 | 3600 | 3600 | 0 | 0 | 0
0.35 | 6.5973 | 73575 | 7875.1361 |  | 9 | 4050 | 4050 | 4050 | 0 | 0 | 0
0.375 | 7.0686 | 73575 | 8643.9131 |  | 10 | 4500 | 4500 | 4500 | 0 | 0 | 0
0.4 | 7.5398 | 73575 | 9440.1923 |  | 11 | 4950 | 4950 | 4950 | 0 | 0 | 0
0.425 | 8.0111 | 73575 | 10263.9739 |  | 12 | 5400 | 5400 | 5400 | 0 | 0 | 0
0.45 | 8.4823 | 73575 | 11115.2577 |  | 13 | 5850 | 5850 | 5850 | 0 | 0 | 0
0.475 | 8.9535 | 73575 | 11994.0439 |  | 14 | 6300 | 6300 | 6300 | 0 | 0 | 0
0.5 | 9.4248 | 73575 | 12900.3323 |  | 15 | 6750 | 6750 | 6750 | 0 | 0 | 0
0.525 | 9.896 | 73575 | 13834.123 |  | 16 | 7200 | 7200 | 7200 | 0 | 0 | 0
0.55 | 10.3673 | 73575 | 14795.4161 |  | 17 | 7650 | 7650 | 7650 | 0 | 0 | 0
0.575 | 10.8385 | 73575 | 15784.2114 |  | 18 | 8100 | 8100 | 8100 | 0 | 0 | 0
0.6 | 11.3097 | 73575 | 16800.509 |  | 19 | 8550 | 8550 | 8550 | 0 | 0 | 0
0.625 | 11.781 | 73575 | 17844.309 |  | 20 | 9000 | 9000 | 9000 | 0 | 0 | 0
0.65 | 12.2522 | 73575 | 18915.6112 |  | 21 | 9450 | 9450 | 9450 | 0 | 0 | 0
0.675 | 12.7235 | 73575 | 20014.4157 |  | 22 | 9900 | 9900 | 9900 | 0 | 0 | 0
0.7 | 13.1947 | 73575 | 21140.7226 |  | 23 | 10350 | 10350 | 10350 | 0 | 0 | 0
0.725 | 13.6659 | 73575 | 22294.5317 |  | 24 | 10800 | 10800 | 10800 | 0 | 0 | 0
0.75 | 14.1372 | 73575 | 23475.8431 |  | 25 | 11250 | 11250 | 11250 | 0 | 0 | 0
0.775 | 14.6084 | 73575 | 24684.6568 |  | 26 | 11700 | 11700 | 11700 | 0 | 0 | 0
0.8 | 15.0796 | 73575 | 25920.9728 |  | 27 | 12150 | 12150 | 12150 | 0 | 0 | 0
0.825 | 15.5509 | 73575 | 27184.7911 |  | 28 | 12600 | 12600 | 12600 | 0 | 0 | 0
0.85 | 16.0221 | 73575 | 28476.1118 |  | 29 | 13050 | 13050 | 13050 | 0 | 0 | 0
0.875 | 16.4934 | 73575 | 29794.9347 |  | 30 | 13500 | 13500 | 13500 | 0 | 0 | 0
0.9 | 16.9646 | 73575 | 31141.2599 |  | 31 | 13950 | 13950 | 13950 | 0 | 0 | 0
0.925 | 17.4358 | 73575 | 32515.0874 |  | 32 | 14400 | 14400 | 14400 | 0 | 0 | 0
0.95 | 17.9071 | 73575 | 33916.4172 |  | 33 | 14850 | 14850 | 14850 | 0 | 0 | 0
0.975 | 18.3783 | 73575 | 35345.2493 |  | 34 | 15300 | 15300 | 15300 | 0 | 0 | 0
1 | 18.8496 | 73575 | 36801.5837 |  | 35 | 15750 | 15750 | 15750 | 0 | 0 | 0
1.025 | 19.3208 | 73575 | 38285.4204 |  | 36 | 16200 | 16200 | 16200 | 0 | 0 | 0
1.05 | 19.792 | 73575 | 39796.7594 |  | 37 | 16650 | 16650 | 16650 | 0 | 0 | 0
1.075 | 20.2633 | 73575 | 41335.6006 |  | 38 | 17100 | 17100 | 17100 | 0 | 0 | 0
1.1 | 20.7345 | 73575 | 42901.9442 |  | 39 | 17550 | 17550 | 17550 | 0 | 0 | 0
1.125 | 21.2058 | 73575 | 44495.7901 |  | 40 | 18000 | 18000 | 18000 | 0 | 0 | 0
1.15 | 21.677 | 73575 | 46117.1383 |  | 41 | 18450 | 18450 | 18450 | 0 | 0 | 0
1.175 | 22.1482 | 73575 | 47765.9888 |  | 42 | 18900 | 18900 | 18900 | 0 | 0 | 0
1.2 | 22.6195 | 73575 | 49442.3416 |  | 43 | 19350 | 19350 | 19350 | 0 | 0 | 0
1.225 | 23.0907 | 73575 | 51146.1966 |  | 44 | 19800 | 19800 | 19800 | 0 | 0 | 0
1.25 | 23.5619 | 73575 | 52877.554 |  | 45 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
1.275 | 24.0332 | 73575 | 54636.4137 |  | 46 | 900 | 900 | 900 | 0 | 0 | 0
1.3 | 24.5044 | 73575 | 56422.7756 |  | 47 | 1350 | 1350 | 1350 | 0 | 0 | 0
1.325 | 24.9757 | 73575 | 58236.6399 |  | 48 | 1800 | 1800 | 1800 | 0 | 0 | 0
1.35 | 25.4469 | 73575 | 60078.0065 |  | 49 | 2250 | 2250 | 2250 | 0 | 0 | 0
1.375 | 25.9181 | 73575 | 61946.8753 |  | 50 | 2700 | 2700 | 2700 | 0 | 0 | 0
1.4 | 26.3894 | 73575 | 63843.2465 |  | 51 | 3150 | 3150 | 3150 | 0 | 0 | 0
1.425 | 26.8606 | 73575 | 65767.1199 |  | 52 | 3600 | 3600 | 3600 | 0 | 0 | 0
1.45 | 27.3319 | 73575 | 67718.4957 |  | 53 | 4050 | 4050 | 4050 | 0 | 0 | 0
1.475 | 27.8031 | 73575 | 69697.3738 |  | 54 | 4500 | 4500 | 4500 | 0 | 0 | 0
1.5 | 28.2743 | 73575 | 71703.7541 |  | 55 | 4950 | 4950 | 4950 | 0 | 0 | 0
1.525 | 28.7456 | 73575 | 73737.6367 |  | 56 | 5400 | 5400 | 5400 | 0 | 0 | 0
1.55 | 29.2168 | 73575 | 75799.0217 |  | 57 | 5850 | 5850 | 5850 | 0 | 0 | 0
1.575 | 29.6881 | 73575 | 77887.9089 |  | 58 | 6300 | 6300 | 6300 | 0 | 0 | 0
1.6 | 30.1593 | 73575 | 80004.2985 |  | 59 | 6750 | 6750 | 6750 | 0 | 0 | 0
1.625 | 30.6305 | 73575 | 82148.1903 |  | 60 | 7200 | 7200 | 7200 | 0 | 0 | 0
1.65 | 31.1018 | 73575 | 84319.5844 |  | 61 | 7650 | 7650 | 7650 | 0 | 0 | 0
1.675 | 31.573 | 73575 | 86518.4809 |  | 62 | 8100 | 8100 | 8100 | 0 | 0 | 0
1.7 | 32.0442 | 73575 | 88744.8796 |  | 63 | 8550 | 8550 | 8550 | 0 | 0 | 0
1.725 | 32.5155 | 73575 | 90998.7806 |  | 64 | 9000 | 9000 | 9000 | 0 | 0 | 0
1.75 | 32.9867 | 73575 | 93280.184 |  | 65 | 9450 | 9450 | 9450 | 0 | 0 | 0
1.775 | 33.458 | 73575 | 95589.0896 |  | 66 | 9900 | 9900 | 9900 | 0 | 0 | 0
1.8 | 33.9292 | 73575 | 97925.4975 |  | 67 | 10350 | 10350 | 10350 | 0 | 0 | 0
1.825 | 34.4004 | 73575 | 100289.4077 |  | 68 | 10800 | 10800 | 10800 | 0 | 0 | 0
1.85 | 34.8717 | 73575 | 102680.8203 |  | 69 | 11250 | 11250 | 11250 | 0 | 0 | 0
1.875 | 35.3429 | 73575 | 105099.7351 |  | 70 | 11700 | 11700 | 11700 | 0 | 0 | 0
1.9 | 35.8142 | 73575 | 107546.1522 |  | 71 | 12150 | 12150 | 12150 | 0 | 0 | 0
1.925 | 36.2854 | 73575 | 110020.0716 |  | 72 | 12600 | 12600 | 12600 | 0 | 0 | 0
1.95 | 36.7566 | 73575 | 112521.4933 |  | 73 | 13050 | 13050 | 13050 | 0 | 0 | 0
1.975 | 37.2279 | 73575 | 115050.4173 |  | 74 | 13500 | 13500 | 13500 | 0 | 0 | 0
2 | 37.6991 | 73575 | 117606.8436 |  | 75 | 13950 | 13950 | 13950 | 0 | 0 | 0
2.025 | 38.1704 | 73575 | 120190.7722 |  | 76 | 14400 | 14400 | 14400 | 0 | 0 | 0
2.05 | 38.6416 | 73575 | 122802.2031 |  | 77 | 14850 | 14850 | 14850 | 0 | 0 | 0
2.075 | 39.1128 | 73575 | 125441.1363 |  | 78 | 15300 | 15300 | 15300 | 0 | 0 | 0
2.1 | 39.5841 | 73575 | 128107.5718 |  | 79 | 15750 | 15750 | 15750 | 0 | 0 | 0
2.125 | 40.0553 | 73575 | 130801.5096 |  | 80 | 16200 | 16200 | 16200 | 0 | 0 | 0
2.15 | 40.5265 | 73575 | 133522.9497 |  | 81 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 82 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 83 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 84 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 85 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 86 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 87 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 88 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 89 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 90 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 91 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 92 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 93 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 94 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 95 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 96 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 97 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 98 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 99 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 100 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 101 | 5850 | 5850 | 5850 | 0 | 0 | 0
[5 empty] | 102 | 6300 | 6300 | 6300 | 0 | 0 | 0
[5 empty] | 103 | 6750 | 6750 | 6750 | 0 | 0 | 0
[5 empty] | 104 | 7200 | 7200 | 7200 | 0 | 0 | 0
[5 empty] | 105 | 7650 | 7650 | 7650 | 0 | 0 | 0
[5 empty] | 106 | 8100 | 8100 | 8100 | 0 | 0 | 0
[5 empty] | 107 | 8550 | 8550 | 8550 | 0 | 0 | 0
[5 empty] | 108 | 9000 | 9000 | 9000 | 0 | 0 | 0
[5 empty] | 109 | 9450 | 9450 | 9450 | 0 | 0 | 0
[5 empty] | 110 | 9900 | 9900 | 9900 | 0 | 0 | 0
[5 empty] | 111 | 10350 | 10350 | 10350 | 0 | 0 | 0
[5 empty] | 112 | 10800 | 10800 | 10800 | 0 | 0 | 0
[5 empty] | 113 | 11250 | 11250 | 11250 | 0 | 0 | 0
[5 empty] | 114 | 11700 | 11700 | 11700 | 0 | 0 | 0
[5 empty] | 115 | 12150 | 12150 | 12150 | 0 | 0 | 0
[5 empty] | 116 | 12600 | 12600 | 12600 | 0 | 0 | 0
[5 empty] | 117 | 13050 | 13050 | 13050 | 0 | 0 | 0
[5 empty] | 118 | 13500 | 13500 | 13500 | 0 | 0 | 0
[5 empty] | 119 | 13950 | 13950 | 13950 | 0 | 0 | 0
[5 empty] | 120 | 14400 | 14400 | 14400 | 0 | 0 | 0
[5 empty] | 121 | 14850 | 14850 | 14850 | 0 | 0 | 0
[5 empty] | 122 | 15300 | 15300 | 15300 | 0 | 0 | 0
[5 empty] | 123 | 15750 | 15750 | 15750 | 0 | 0 | 0
[5 empty] | 124 | 16200 | 16200 | 16200 | 0 | 0 | 0
[5 empty] | 125 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 126 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 127 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 128 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 129 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 130 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 131 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 132 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 133 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 134 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 135 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 136 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 137 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 138 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 139 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 140 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 141 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 142 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 143 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 144 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 145 | 5850 | 5850 | 5850 | 0 | 0 | 0
[5 empty] | 146 | 6300 | 6300 | 6300 | 0 | 0 | 0
[5 empty] | 147 | 6750 | 6750 | 6750 | 0 | 0 | 0
[5 empty] | 148 | 7200 | 7200 | 7200 | 0 | 0 | 0
[5 empty] | 149 | 7650 | 7650 | 7650 | 0 | 0 | 0
[5 empty] | 150 | 8100 | 8100 | 8100 | 0 | 0 | 0
[5 empty] | 151 | 8550 | 8550 | 8550 | 0 | 0 | 0
[5 empty] | 152 | 9000 | 9000 | 9000 | 0 | 0 | 0
[5 empty] | 153 | 9450 | 9450 | 9450 | 0 | 0 | 0
[5 empty] | 154 | 9900 | 9900 | 9900 | 0 | 0 | 0
[5 empty] | 155 | 10350 | 10350 | 10350 | 0 | 0 | 0
[5 empty] | 156 | 10800 | 10800 | 10800 | 0 | 0 | 0
[5 empty] | 157 | 11250 | 11250 | 11250 | 0 | 0 | 0
[5 empty] | 158 | 11700 | 11700 | 11700 | 0 | 0 | 0
[5 empty] | 159 | 12150 | 12150 | 12150 | 0 | 0 | 0
[5 empty] | 160 | 12600 | 12600 | 12600 | 0 | 0 | 0
[5 empty] | 161 | 13050 | 13050 | 13050 | 0 | 0 | 0
[5 empty] | 162 | 13500 | 13500 | 13500 | 0 | 0 | 0
[5 empty] | 163 | 13950 | 13950 | 13950 | 0 | 0 | 0
[5 empty] | 164 | 14400 | 14400 | 14400 | 0 | 0 | 0
[5 empty] | 165 | 14850 | 14850 | 14850 | 0 | 0 | 0
[5 empty] | 166 | 15300 | 15300 | 15300 | 0 | 0 | 0
[5 empty] | 167 | 15750 | 15750 | 15750 | 0 | 0 | 0
[5 empty] | 168 | 16200 | 16200 | 16200 | 0 | 0 | 0
[5 empty] | 169 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 170 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 171 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 172 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 173 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 174 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 175 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 176 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 177 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 178 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 179 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 180 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 181 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 182 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 183 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 184 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 185 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 186 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 187 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 188 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 189 | 5850 | 5850 | 5850 | 0 | 0 | 0
[5 empty] | 190 | 6300 | 6300 | 6300 | 0 | 0 | 0
[5 empty] | 191 | 6750 | 6750 | 6750 | 0 | 0 | 0
[5 empty] | 192 | 7200 | 7200 | 7200 | 0 | 0 | 0
[5 empty] | 193 | 7650 | 7650 | 7650 | 0 | 0 | 0
[5 empty] | 194 | 8100 | 8100 | 8100 | 0 | 0 | 0
[5 empty] | 195 | 8550 | 8550 | 8550 | 0 | 0 | 0
[5 empty] | 196 | 9000 | 9000 | 9000 | 0 | 0 | 0
[5 empty] | 197 | 9450 | 9450 | 9450 | 0 | 0 | 0
[5 empty] | 198 | 9900 | 9900 | 9900 | 0 | 0 | 0
[5 empty] | 199 | 10350 | 10350 | 10350 | 0 | 0 | 0
[5 empty] | 200 | 10800 | 10800 | 10800 | 0 | 0 | 0
[5 empty] | 201 | 11250 | 11250 | 11250 | 0 | 0 | 0
[5 empty] | 202 | 11700 | 11700 | 11700 | 0 | 0 | 0
[5 empty] | 203 | 12150 | 12150 | 12150 | 0 | 0 | 0
[5 empty] | 204 | 12600 | 12600 | 12600 | 0 | 0 | 0
[5 empty] | 205 | 13050 | 13050 | 13050 | 0 | 0 | 0
[5 empty] | 206 | 13500 | 13500 | 13500 | 0 | 0 | 0
[5 empty] | 207 | 13950 | 13950 | 13950 | 0 | 0 | 0
[5 empty] | 208 | 14400 | 14400 | 14400 | 0 | 0 | 0
[5 empty] | 209 | 14850 | 14850 | 14850 | 0 | 0 | 0
[5 empty] | 210 | 15300 | 15300 | 15300 | 0 | 0 | 0
[5 empty] | 211 | 15750 | 15750 | 15750 | 0 | 0 | 0
[5 empty] | 212 | 16200 | 16200 | 16200 | 0 | 0 | 0
[5 empty] | 213 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 214 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 215 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 216 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 217 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 218 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 219 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 220 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 221 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 222 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 223 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 224 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 225 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 226 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 227 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 228 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 229 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 230 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 231 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 232 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 233 | 5850 | 5850 | 5850 | 0 | 0 | 0
[5 empty] | 234 | 6300 | 6300 | 6300 | 0 | 0 | 0
[5 empty] | 235 | 6750 | 6750 | 6750 | 0 | 0 | 0
[5 empty] | 236 | 7200 | 7200 | 7200 | 0 | 0 | 0
[5 empty] | 237 | 7650 | 7650 | 7650 | 0 | 0 | 0
[5 empty] | 238 | 8100 | 8100 | 8100 | 0 | 0 | 0
[5 empty] | 239 | 8550 | 8550 | 8550 | 0 | 0 | 0
[5 empty] | 240 | 9000 | 9000 | 9000 | 0 | 0 | 0
[5 empty] | 241 | 9450 | 9450 | 9450 | 0 | 0 | 0
[5 empty] | 242 | 9900 | 9900 | 9900 | 0 | 0 | 0
[5 empty] | 243 | 10350 | 10350 | 10350 | 0 | 0 | 0
[5 empty] | 244 | 10800 | 10800 | 10800 | 0 | 0 | 0
[5 empty] | 245 | 11250 | 11250 | 11250 | 0 | 0 | 0
[5 empty] | 246 | 11700 | 11700 | 11700 | 0 | 0 | 0
[5 empty] | 247 | 12150 | 12150 | 12150 | 0 | 0 | 0
[5 empty] | 248 | 12600 | 12600 | 12600 | 0 | 0 | 0
[5 empty] | 249 | 13050 | 13050 | 13050 | 0 | 0 | 0
[5 empty] | 250 | 13500 | 13500 | 13500 | 0 | 0 | 0
[5 empty] | 251 | 13950 | 13950 | 13950 | 0 | 0 | 0
[5 empty] | 252 | 14400 | 14400 | 14400 | 0 | 0 | 0
[5 empty] | 253 | 14850 | 14850 | 14850 | 0 | 0 | 0
[5 empty] | 254 | 15300 | 15300 | 15300 | 0 | 0 | 0
[5 empty] | 255 | 15750 | 15750 | 15750 | 0 | 0 | 0
[5 empty] | 256 | 16200 | 16200 | 16200 | 0 | 0 | 0
[5 empty] | 257 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 258 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 259 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 260 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 261 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 262 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 263 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 264 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 265 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 266 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 267 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 268 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 269 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 270 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 271 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 272 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 273 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 274 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 275 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 276 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 277 | 5850 | 5850 | 5850 | 0 | 0 | 0
[5 empty] | 278 | 6300 | 6300 | 6300 | 0 | 0 | 0
[5 empty] | 279 | 6750 | 6750 | 6750 | 0 | 0 | 0
[5 empty] | 280 | 7200 | 7200 | 7200 | 0 | 0 | 0
[5 empty] | 281 | 7650 | 7650 | 7650 | 0 | 0 | 0
[5 empty] | 282 | 8100 | 8100 | 8100 | 0 | 0 | 0
[5 empty] | 283 | 8550 | 8550 | 8550 | 0 | 0 | 0
[5 empty] | 284 | 9000 | 9000 | 9000 | 0 | 0 | 0
[5 empty] | 285 | 9450 | 9450 | 9450 | 0 | 0 | 0
[5 empty] | 286 | 9900 | 9900 | 9900 | 0 | 0 | 0
[5 empty] | 287 | 10350 | 10350 | 10350 | 0 | 0 | 0
[5 empty] | 288 | 10800 | 10800 | 10800 | 0 | 0 | 0
[5 empty] | 289 | 11250 | 11250 | 11250 | 0 | 0 | 0
[5 empty] | 290 | 11700 | 11700 | 11700 | 0 | 0 | 0
[5 empty] | 291 | 12150 | 12150 | 12150 | 0 | 0 | 0
[5 empty] | 292 | 12600 | 12600 | 12600 | 0 | 0 | 0
[5 empty] | 293 | 13050 | 13050 | 13050 | 0 | 0 | 0
[5 empty] | 294 | 13500 | 13500 | 13500 | 0 | 0 | 0
[5 empty] | 295 | 13950 | 13950 | 13950 | 0 | 0 | 0
[5 empty] | 296 | 14400 | 14400 | 14400 | 0 | 0 | 0
[5 empty] | 297 | 14850 | 14850 | 14850 | 0 | 0 | 0
[5 empty] | 298 | 15300 | 15300 | 15300 | 0 | 0 | 0
[5 empty] | 299 | 15750 | 15750 | 15750 | 0 | 0 | 0
[5 empty] | 300 | 16200 | 16200 | 16200 | 0 | 0 | 0
[5 empty] | 301 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 302 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 303 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 304 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 305 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 306 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 307 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 308 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 309 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 310 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 311 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 312 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 313 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 314 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 315 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 316 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 317 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 318 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 319 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 320 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 321 | 5850 | 5850 | 5850 | 0 | 0 | 0
[5 empty] | 322 | 6300 | 6300 | 6300 | 0 | 0 | 0
[5 empty] | 323 | 6750 | 6750 | 6750 | 0 | 0 | 0
[5 empty] | 324 | 7200 | 7200 | 7200 | 0 | 0 | 0
[5 empty] | 325 | 7650 | 7650 | 7650 | 0 | 0 | 0
[5 empty] | 326 | 8100 | 8100 | 8100 | 0 | 0 | 0
[5 empty] | 327 | 8550 | 8550 | 8550 | 0 | 0 | 0
[5 empty] | 328 | 9000 | 9000 | 9000 | 0 | 0 | 0
[5 empty] | 329 | 9450 | 9450 | 9450 | 0 | 0 | 0
[5 empty] | 330 | 9900 | 9900 | 9900 | 0 | 0 | 0
[5 empty] | 331 | 10350 | 10350 | 10350 | 0 | 0 | 0
[5 empty] | 332 | 10800 | 10800 | 10800 | 0 | 0 | 0
[5 empty] | 333 | 11250 | 11250 | 11250 | 0 | 0 | 0
[5 empty] | 334 | 11700 | 11700 | 11700 | 0 | 0 | 0
[5 empty] | 335 | 12150 | 12150 | 12150 | 0 | 0 | 0
[5 empty] | 336 | 12600 | 12600 | 12600 | 0 | 0 | 0
[5 empty] | 337 | 13050 | 13050 | 13050 | 0 | 0 | 0
[5 empty] | 338 | 13500 | 13500 | 13500 | 0 | 0 | 0
[5 empty] | 339 | 13950 | 13950 | 13950 | 0 | 0 | 0
[5 empty] | 340 | 14400 | 14400 | 14400 | 0 | 0 | 0
[5 empty] | 341 | 14850 | 14850 | 14850 | 0 | 0 | 0
[5 empty] | 342 | 15300 | 15300 | 15300 | 0 | 0 | 0
[5 empty] | 343 | 15750 | 15750 | 15750 | 0 | 0 | 0
[5 empty] | 344 | 16200 | 16200 | 16200 | 0 | 0 | 0
[5 empty] | 345 | 16650 | 16650 | 16650 | 0 | 0 | 0
[5 empty] | 346 | 17100 | 17100 | 17100 | 0 | 0 | 0
[5 empty] | 347 | 17550 | 17550 | 17550 | 0 | 0 | 0
[5 empty] | 348 | 18000 | 18000 | 18000 | 0 | 0 | 0
[5 empty] | 349 | 18450 | 18450 | 18450 | 0 | 0 | 0
[5 empty] | 350 | 18900 | 18900 | 18900 | 0 | 0 | 0
[5 empty] | 351 | 19350 | 19350 | 19350 | 0 | 0 | 0
[5 empty] | 352 | 19800 | 19800 | 19800 | 0 | 0 | 0
[5 empty] | 353 | 450 | 450 | 450 | 1 | 1 | 1 | 1 | 185
[5 empty] | 354 | 900 | 900 | 900 | 0 | 0 | 0
[5 empty] | 355 | 1350 | 1350 | 1350 | 0 | 0 | 0
[5 empty] | 356 | 1800 | 1800 | 1800 | 0 | 0 | 0
[5 empty] | 357 | 2250 | 2250 | 2250 | 0 | 0 | 0
[5 empty] | 358 | 2700 | 2700 | 2700 | 0 | 0 | 0
[5 empty] | 359 | 3150 | 3150 | 3150 | 0 | 0 | 0
[5 empty] | 360 | 3600 | 3600 | 3600 | 0 | 0 | 0
[5 empty] | 361 | 4050 | 4050 | 4050 | 0 | 0 | 0
[5 empty] | 362 | 4500 | 4500 | 4500 | 0 | 0 | 0
[5 empty] | 363 | 4950 | 4950 | 4950 | 0 | 0 | 0
[5 empty] | 364 | 5400 | 5400 | 5400 | 0 | 0 | 0
[5 empty] | 365 | 5850 | 5850 | 5850 | 0 | 0 | 0

## Risk Exposures
Health Risk Exposure Factors as a function of Severity and frequency
|  |  | 1 | 2 | 3 | 4
Daily Risk Exposure | 1 | 4 | 4 | 8 | 12 | 16
Weekly Risk Exposure | 12 | 3 | 3 | 6 | 9 | 12
Monthly Risk Exposure | 52 | 2 | 2 | 4 | 6 | 8
Annual Risk Exposure | 360 | 1 | 1 | 2 | 3 | 4
Envirnomental Risk Exposure Factors as a function of Severity and frequency
|  |  | 1 | 2 | 3 | 4
Daily Risk Exposure | 365 | 4 | 4 | 8 | 12 | 16
Weekly Risk Exposure | 52 | 3 | 3 | 6 | 9 | 12
Monthly Risk Exposure | 12 | 2 | 2 | 4 | 6 | 8
Annual Risk Exposure | 1 | 1 | 1 | 2 | 3 | 4
Diesel Risk | Frequency | Severity
|  | Health | Environmental
1.6543 | 49.7183 | 2 | 3
Health Risk Exposure | 3.3087
Environmental Exposure | 4.963
Total Risk | 8.2716
Minimum | 0
Maximum | 32
Satisfaction | 84.4%
Risk for Solar
None

## Pump Data
Distance to storage tank | 13.6015 |  |  | [m]
Height of Storage Tank | 10 |  |  | [m]
Density of Water | 1000 |  |  | [kg/m^3] | Tank Height | 10
Gravity Constant | 9.81 |  |  | [m/s^2] | Distance to Tank x | 2
Pump Coeffiecients | Pump A | Pump B | Pump C |  | Distance to Tank y | 9
| -0.0172 | -0.0039 | -0.0151 | a | Distance to tank | 13.6015
| -0.3605 | -0.096 | -0.5516 | b | Cost | 612.0662
| 150.9 | 237.86 | 356.8 | c
Diameter of Pipe | 0.03 |  |  | [m]
Friction Factor | 0.05
K | 10
Pump A
Q_in | Flow Velocity | Pump Pressure | System Pressure
[LPM] | [m/s] | [kPa] | [kPa]
0 | 0 | 150.9 | 98.1
10 | 0.23579 | 145.575 | 99.0081
20 | 0.47157 | 136.81 | 101.7325
30 | 0.70736 | 124.605 | 106.273
40 | 0.94314 | 108.96 | 112.6298
50 | 1.1789 | 89.875 | 120.8028
57 | 1.344 | 74.4687 | 127.6046
60 | 1.4147 | 67.35 | 130.7921
70 | 1.6505 | 41.385 | 142.5976
80 | 1.8863 | 11.98 | 156.2193
90 | 2.1221 | 0 | 171.6572
97.23 | 2.2925 | 0 | 183.9501
105.5 | 2.4875 | 0 | 199.1753
105 | 2.4757 | 0 | 198.2195
110 | 2.5936 | 0 | 207.9817
120 | 2.8294 | 0 | 228.8683
130 | 3.0652 | 0 | 251.5712
140 | 3.301 | 0 | 276.0902
150 | 3.5368 | 0 | 302.4255
Pump B
Q_in | Flow Velocity | Pump Pressure | System Pressure
[LPM] | [m/s] | [kPa] | [kPa]
0 | 0 | 237.86 | 98.1
10 | 0.23579 | 236.51 | 99.0081
20 | 0.47157 | 234.38 | 101.7325
30 | 0.70736 | 231.47 | 106.273
40 | 0.94314 | 227.78 | 112.6298
50 | 1.1789 | 223.31 | 120.8028
57 | 1.344 | 219.7169 | 127.6046
60 | 1.4147 | 218.06 | 130.7921
70 | 1.6505 | 212.03 | 142.5976
80 | 1.8863 | 205.22 | 156.2193
90 | 2.1221 | 197.63 | 171.6572
100 | 2.3579 | 189.26 | 188.9113
105.5 | 2.4875 | 184.324 | 199.1753
105 | 2.4757 | 184.7825 | 198.2195
110 | 2.5936 | 180.11 | 207.9817
120 | 2.8294 | 170.18 | 228.8683
130 | 3.0652 | 159.47 | 251.5712
140 | 3.301 | 147.98 | 276.0902
150 | 3.5368 | 135.71 | 302.4255
Pump C
Q_in | Flow Velocity | Pump Pressure | System Pressure
[LPM] | [m/s] | [kPa] | [kPa]
0 | 0 | 356.8 | 98.1
10 | 0.23579 | 349.774 | 99.0081
20 | 0.47157 | 339.728 | 101.7325
30 | 0.70736 | 326.662 | 106.273
40 | 0.94314 | 310.576 | 112.6298
50 | 1.1789 | 291.47 | 120.8028
57 | 1.344 | 276.2989 | 127.6046
60 | 1.4147 | 269.344 | 130.7921
70 | 1.6505 | 244.198 | 142.5976
80 | 1.8863 | 216.032 | 156.2193
90 | 2.1221 | 184.846 | 171.6572
97.23 | 2.2925 | 160.4175 | 183.9501
105.5 | 2.4875 | 130.5394 | 199.1753
105 | 2.4757 | 132.4045 | 198.2195
110 | 2.5936 | 113.414 | 207.9817
120 | 2.8294 | 73.168 | 228.8683
130 | 3.0652 | 29.902 | 251.5712
140 | 3.301 | 0 | 276.0902
150 | 3.5368 | 0 | 302.4255

## Land Use
Land Use Satifaction
100%

## Overall Satisfaction
Generatior |  |  |  | Solar
Attribute | Weight | % |  | Attribute | Weight | %
Consumption | 15% | 65.18% | 9.778% | Consumption | 15% | 65.18% | 9.778%
Relative Cost | 25% | 93.88% | 23.47% | Relative Cost | 25% | 92.4% | 23.1%
Health and Environmental Risk | 10% | 84.4% | 8.44% | Health and Environmental Risk | 10% | 100% | 10%
Power System GHG Emissions | 10% | 28.27% | 2.827% | Power System GHG Emissions | 10% | 70.44% | 7.044%
Maintainance Occurances | 20% | 99.64% | 19.93% | Maintainance Occurances | 20% | 98.87% | 19.77%
On demand flow rate | 5% | 58.75% | 2.938% | On demand flow rate | 5% | 58.75% | 2.938%
Reliabilty | 10% | 95.32% | 9.532% | Reliabilty | 10% | 95.32% | 9.532%
Land Use | 5% | 100% | 5% | Land Use | 5% | 100% | 5%
| Total |  | 81.91% |  | Total |  | 87.17%

## Weather Data - 2014-2015
Area of Roof (A_c) | 100 | m^2 |  | S(C)=99% | 675
Capacity of Catchment Tank | 2.5 | m^3 |  | S(C)=50% | 395
Capacity of tank (V_tank) | 35 | m^3 |  | S(C)=1% | 115
Initial Volume of water (V_initial) | 0 | m^3 |  | Overall Satisfaction | 65.18%
Consumption (C) | 450 | L/day
Min. Water Consumption(C_min) | 115 | L/day
Max. Water Consumption(C_max) | 675 | L/day
Cost over 5 years |  |  |  | Cost to ship in water
Area of roof | 350 |  |  | 100000
Storage Tank | 9625
Catchment Tank | 900 |  |  |  | Tower
Shipping in water | 1875 | over 5 years |  | Tower Height (m) | 6.5
Total | 12750 |  |  |  | 5300.1499 | Minimum | 1150
[6 empty] | Maximim | 1825
|  |  |  | Days water shipped in over 5 years | 37.5 | Calculated | 1731.25
Date | Daily Rainfall (mm) | Q_in (m^3/day) | V_water (m^3) | What days does water need to be shipped in | Reliablity | Satisfaction | 95.32%
2014-01-01 | 18.8 | 1.88 | 1.88 |  | 0
2014-01-02 | 19.8 | 1.98 | 3.86 |  | 0
2014-01-03 | 0 | 0 | 3.86 |  | 0
2014-01-04 | 0 | 0 | 3.86 |  | 0
2014-01-05 | 0 | 0 | 3.86 |  | 0
2014-01-06 | 5 | 0.5 | 4.36 |  | 0
2014-01-07 | 20.4 | 2.04 | 6.4 |  | 0
2014-01-08 | 24.8 | 2.48 | 8.88 |  | 0
2014-01-09 | 34 | 2.5 | 11.38 |  | 0
2014-01-10 | 44.6 | 2.5 | 13.88 |  | 0
2014-01-11 | 14.4 | 1.44 | 15.32 |  | 0
2014-01-12 | 50.2 | 2.5 | 17.82 |  | 0
2014-01-13 | 9.6 | 0.96 | 18.78 |  | 0
2014-01-14 | 5.8 | 0.58 | 19.36 |  | 0
2014-01-15 | 1.6 | 0.16 | 19.52 |  | 0
2014-01-16 | 0.8 | 0.08 | 19.6 |  | 0
2014-01-17 | 0 | 0 | 19.6 |  | 0
2014-01-18 | 2.6 | 0.26 | 19.86 |  | 0
2014-01-19 | 1 | 0.1 | 19.96 |  | 0
2014-01-20 | 0.6 | 0.06 | 20.02 |  | 0
2014-01-21 | 0.8 | 0.08 | 20.1 |  | 0
2014-01-22 | 0.6 | 0.06 | 20.16 |  | 0
2014-01-23 | 0 | 0 | 20.16 |  | 0
2014-01-24 | 0 | 0 | 20.16 |  | 0
2014-01-25 | 0 | 0 | 20.16 |  | 0
2014-01-26 | 0 | 0 | 20.16 |  | 0
2014-01-27 | 17.6 | 1.76 | 21.92 |  | 0
2014-01-28 | 0 | 0 | 21.92 |  | 0
2014-01-29 | 0 | 0 | 21.92 |  | 0
2014-01-30 | 0 | 0 | 21.92 |  | 0
2014-01-31 | 2.6 | 0.26 | 22.18 |  | 0
2014-02-01 | 2.6 | 0.26 | 22.44 |  | 0
2014-02-02 | 0 | 0 | 21.99 |  | 0
2014-02-03 | 0 | 0 | 21.54 |  | 0
2014-02-04 | 0 | 0 | 21.09 |  | 0
2014-02-05 | 0 | 0 | 20.64 |  | 0
2014-02-06 | 0 | 0 | 20.19 |  | 0
2014-02-07 | 0 | 0 | 19.74 |  | 0
2014-02-08 | 0 | 0 | 19.29 |  | 0
2014-02-09 | 12.2 | 1.22 | 20.06 |  | 0
2014-02-10 | 13.4 | 1.34 | 20.95 |  | 0
2014-02-11 | 46.6 | 2.5 | 23 |  | 0
2014-02-12 | 16.8 | 1.68 | 24.23 |  | 0
2014-02-13 | 15.6 | 1.56 | 25.34 |  | 0
2014-02-14 | 3 | 0.3 | 25.19 |  | 0
2014-02-15 | 11.6 | 1.16 | 25.9 |  | 0
2014-02-16 | 19 | 1.9 | 27.35 |  | 0
2014-02-17 | 9.2 | 0.92 | 27.82 |  | 0
2014-02-18 | 12.6 | 1.26 | 28.63 |  | 0
2014-02-19 | 21.8 | 2.18 | 30.36 |  | 0
2014-02-20 | 2.4 | 0.24 | 30.15 |  | 0
2014-02-21 | 0.8 | 0.08 | 29.78 |  | 0
2014-02-22 | 4.8 | 0.48 | 29.81 |  | 0
2014-02-23 | 14.6 | 1.46 | 30.82 |  | 0
2014-02-24 | 6.8 | 0.68 | 31.05 |  | 0
2014-02-25 | 0 | 0 | 30.6 |  | 0
2014-02-26 | 0.8 | 0.08 | 30.23 |  | 0
2014-02-27 | 0 | 0 | 29.78 |  | 0
2014-02-28 | 0.4 | 0.04 | 29.37 |  | 0
2014-03-01 | 2 | 0.2 | 29.12 |  | 0
2014-03-02 | 19 | 1.9 | 30.57 |  | 0
2014-03-03 | 1 | 0.1 | 30.22 |  | 0
2014-03-04 | 2.4 | 0.24 | 30.01 |  | 0
2014-03-05 | 23.8 | 2.38 | 31.94 |  | 0
2014-03-06 | 8.6 | 0.86 | 32.35 |  | 0
2014-03-07 | 34 | 2.5 | 34.4 |  | 0
2014-03-08 | 52.4 | 2.5 | 35 |  | 0
2014-03-09 | 10.6 | 1.06 | 35 |  | 0
2014-03-10 | 2.4 | 0.24 | 34.79 |  | 0
2014-03-11 | 0 | 0 | 34.34 |  | 0
2014-03-12 | 2.8 | 0.28 | 34.17 |  | 0
2014-03-13 | 20.2 | 2.02 | 35 |  | 0
2014-03-14 | 13.8 | 1.38 | 35 |  | 0
2014-03-15 | 22.8 | 2.28 | 35 |  | 0
2014-03-16 | 5.4 | 0.54 | 35 |  | 0
2014-03-17 | 0.4 | 0.04 | 34.59 |  | 0
2014-03-18 | 31 | 2.5 | 35 |  | 0
2014-03-19 | 1.6 | 0.16 | 34.71 |  | 0
2014-03-20 | 1.6 | 0.16 | 34.42 |  | 0
2014-03-21 | 7.6 | 0.76 | 34.73 |  | 0
2014-03-22 | 2.6 | 0.26 | 34.54 |  | 0
2014-03-23 | 0 | 0 | 34.09 |  | 0
2014-03-24 | 4 | 0.4 | 34.04 |  | 0
2014-03-25 | 31 | 2.5 | 35 |  | 0
2014-03-26 | 0.2 | 0.02 | 34.57 |  | 0
2014-03-27 | 4.4 | 0.44 | 34.56 |  | 0
2014-03-28 | 23.6 | 2.36 | 35 |  | 0
2014-03-29 | 41.6 | 2.5 | 35 |  | 0
2014-03-30 | 3 | 0.3 | 34.85 |  | 0
2014-03-31 | 0 | 0 | 34.4 |  | 0
2014-04-01 | 0 | 0 | 33.95 |  | 0
2014-04-02 | 5.6 | 0.56 | 34.06 |  | 0
2014-04-03 | 20.4 | 2.04 | 35 |  | 0
2014-04-04 | 2.6 | 0.26 | 34.81 |  | 0
2014-04-05 | 15.9 | 1.59 | 35 |  | 0
2014-04-06 | 9.4 | 0.94 | 35 |  | 0
2014-04-07 | 13.6 | 1.36 | 35 |  | 0
2014-04-08 | 5.6 | 0.56 | 35 |  | 0
2014-04-09 | 0 | 0 | 34.55 |  | 0
2014-04-10 | 16.6 | 1.66 | 35 |  | 0
2014-04-11 | 0 | 0 | 34.55 |  | 0
2014-04-12 | 0 | 0 | 34.1 |  | 0
2014-04-13 | 0 | 0 | 33.65 |  | 0
2014-04-14 | 14.8 | 1.48 | 34.68 |  | 0
2014-04-15 | 20.8 | 2.08 | 35 |  | 0
2014-04-16 | 37.4 | 2.5 | 35 |  | 0
2014-04-17 | 9.8 | 0.98 | 35 |  | 0
2014-04-18 | 1.9 | 0.19 | 34.74 |  | 0
2014-04-19 | 21 | 2.1 | 35 |  | 0
2014-04-20 | 30 | 2.5 | 35 |  | 0
2014-04-21 | 0 | 0 | 34.55 |  | 0
2014-04-22 | 4.4 | 0.44 | 34.54 |  | 0
2014-04-23 | 12.8 | 1.28 | 35 |  | 0
2014-04-24 | 26 | 2.5 | 35 |  | 0
2014-04-25 | 1.8 | 0.18 | 34.73 |  | 0
2014-04-26 | 35 | 2.5 | 35 |  | 0
2014-04-27 | 7.2 | 0.72 | 35 |  | 0
2014-04-28 | 0.8 | 0.08 | 34.63 |  | 0
2014-04-29 | 0.1 | 0.01 | 34.19 |  | 0
2014-04-30 | 0 | 0 | 33.74 |  | 0
2014-05-01 | 0 | 0 | 33.29 |  | 0
2014-05-02 | 2 | 0.2 | 33.04 |  | 0
2014-05-03 | 4.6 | 0.46 | 33.05 |  | 0
2014-05-04 | 3.8 | 0.38 | 32.98 |  | 0
2014-05-05 | 0 | 0 | 32.53 |  | 0
2014-05-06 | 0 | 0 | 32.08 |  | 0
2014-05-07 | 0 | 0 | 31.63 |  | 0
2014-05-08 | 0 | 0 | 31.18 |  | 0
2014-05-09 | 0 | 0 | 30.73 |  | 0
2014-05-10 | 0.2 | 0.02 | 30.3 |  | 0
2014-05-11 | 0 | 0 | 29.85 |  | 0
2014-05-12 | 0.2 | 0.02 | 29.42 |  | 0
2014-05-13 | 0 | 0 | 28.97 |  | 0
2014-05-14 | 0 | 0 | 28.52 |  | 0
2014-05-15 | 0 | 0 | 28.07 |  | 0
2014-05-16 | 2.8 | 0.28 | 27.9 |  | 0
2014-05-17 | 0 | 0 | 27.45 |  | 0
2014-05-18 | 0 | 0 | 27 |  | 0
2014-05-19 | 0 | 0 | 26.55 |  | 0
2014-05-20 | 0 | 0 | 26.1 |  | 0
2014-05-21 | 8.2 | 0.82 | 26.47 |  | 0
2014-05-22 | 29.6 | 2.5 | 28.52 |  | 0
2014-05-23 | 0.8 | 0.08 | 28.15 |  | 0
2014-05-24 | 5.2 | 0.52 | 28.22 |  | 0
2014-05-25 | 23.4 | 2.34 | 30.11 |  | 0
2014-05-26 | 0 | 0 | 29.66 |  | 0
2014-05-27 | 4.4 | 0.44 | 29.65 |  | 0
2014-05-28 | 0 | 0 | 29.2 |  | 0
2014-05-29 | 0 | 0 | 28.75 |  | 0
2014-05-30 | 0 | 0 | 28.3 |  | 0
2014-05-31 | 0 | 0 | 27.85 |  | 0
2014-06-01 | 0 | 0 | 27.4 |  | 0
2014-06-02 | 0 | 0 | 26.95 |  | 0
2014-06-03 | 0 | 0 | 26.5 |  | 0
2014-06-04 | 0 | 0 | 26.05 |  | 0
2014-06-05 | 0 | 0 | 25.6 |  | 0
2014-06-06 | 0 | 0 | 25.15 |  | 0
2014-06-07 | 0 | 0 | 24.7 |  | 0
2014-06-08 | 0.2 | 0.02 | 24.27 |  | 0
2014-06-09 | 0 | 0 | 23.82 |  | 0
2014-06-10 | 0 | 0 | 23.37 |  | 0
2014-06-11 | 0 | 0 | 22.92 |  | 0
2014-06-12 | 0 | 0 | 22.47 |  | 0
2014-06-13 | 0 | 0 | 22.02 |  | 0
2014-06-14 | 3.6 | 0.36 | 21.93 |  | 0
2014-06-15 | 0 | 0 | 21.48 |  | 0
2014-06-16 | 0 | 0 | 21.03 |  | 0
2014-06-17 | 0 | 0 | 20.58 |  | 0
2014-06-18 | 1.6 | 0.16 | 20.29 |  | 0
2014-06-19 | 20.8 | 2.08 | 21.92 |  | 0
2014-06-20 | 3.2 | 0.32 | 21.79 |  | 0
2014-06-21 | 1.2 | 0.12 | 21.46 |  | 0
2014-06-22 | 0 | 0 | 21.01 |  | 0
2014-06-23 | 15.4 | 1.54 | 22.1 |  | 0
2014-06-24 | 1.2 | 0.12 | 21.77 |  | 0
2014-06-25 | 0 | 0 | 21.32 |  | 0
2014-06-26 | 5.8 | 0.58 | 21.45 |  | 0
2014-06-27 | 20.4 | 2.04 | 23.04 |  | 0
2014-06-28 | 20.4 | 2.04 | 24.63 |  | 0
2014-06-29 | 0.6 | 0.06 | 24.24 |  | 0
2014-06-30 | 0 | 0 | 23.79 |  | 0
2014-07-01 | 0 | 0 | 23.34 |  | 0
2014-07-02 | 1.8 | 0.18 | 23.07 |  | 0
2014-07-03 | 6.2 | 0.62 | 23.24 |  | 0
2014-07-04 | 9.4 | 0.94 | 23.73 |  | 0
2014-07-05 | 26.6 | 2.5 | 25.78 |  | 0
2014-07-06 | 13.6 | 1.36 | 26.69 |  | 0
2014-07-07 | 0 | 0 | 26.24 |  | 0
2014-07-08 | 0 | 0 | 25.79 |  | 0
2014-07-09 | 0 | 0 | 25.34 |  | 0
2014-07-10 | 0 | 0 | 24.89 |  | 0
2014-07-11 | 0 | 0 | 24.44 |  | 0
2014-07-12 | 0 | 0 | 23.99 |  | 0
2014-07-13 | 0 | 0 | 23.54 |  | 0
2014-07-14 | 0 | 0 | 23.09 |  | 0
2014-07-15 | 0 | 0 | 22.64 |  | 0
2014-07-16 | 0 | 0 | 22.19 |  | 0
2014-07-17 | 0 | 0 | 21.74 |  | 0
2014-07-18 | 37 | 2.5 | 23.79 |  | 0
2014-07-19 | 1.8 | 0.18 | 23.52 |  | 0
2014-07-20 | 0 | 0 | 23.07 |  | 0
2014-07-21 | 0 | 0 | 22.62 |  | 0
2014-07-22 | 8 | 0.8 | 22.97 |  | 0
2014-07-23 | 18.2 | 1.82 | 24.34 |  | 0
2014-07-24 | 0.6 | 0.06 | 23.95 |  | 0
2014-07-25 | 0 | 0 | 23.5 |  | 0
2014-07-26 | 0 | 0 | 23.05 |  | 0
2014-07-27 | 0 | 0 | 22.6 |  | 0
2014-07-28 | 0 | 0 | 22.15 |  | 0
2014-07-29 | 0 | 0 | 21.7 |  | 0
2014-07-30 | 0 | 0 | 21.25 |  | 0
2014-07-31 | 0 | 0 | 20.8 |  | 0
2014-08-01 | 0 | 0 | 20.35 |  | 0
2014-08-02 | 0 | 0 | 19.9 |  | 0
2014-08-03 | 0 | 0 | 19.45 |  | 0
2014-08-04 | 0 | 0 | 19 |  | 0
2014-08-05 | 0 | 0 | 18.55 |  | 0
2014-08-06 | 0 | 0 | 18.1 |  | 0
2014-08-07 | 0 | 0 | 17.65 |  | 0
2014-08-08 | 0 | 0 | 17.2 |  | 0
2014-08-09 | 0 | 0 | 16.75 |  | 0
2014-08-10 | 0 | 0 | 16.3 |  | 0
2014-08-11 | 0 | 0 | 15.85 |  | 0
2014-08-12 | 0 | 0 | 15.4 |  | 0
2014-08-13 | 0 | 0 | 14.95 |  | 0
2014-08-14 | 0 | 0 | 14.5 |  | 0
2014-08-15 | 0 | 0 | 14.05 |  | 0
2014-08-16 | 0 | 0 | 13.6 |  | 0
2014-08-17 | 0 | 0 | 13.15 |  | 0
2014-08-18 | 0 | 0 | 12.7 |  | 0
2014-08-19 | 0 | 0 | 12.25 |  | 0
2014-08-20 | 0 | 0 | 11.8 |  | 0
2014-08-21 | 0 | 0 | 11.35 |  | 0
2014-08-22 | 0 | 0 | 10.9 |  | 0
2014-08-23 | 0 | 0 | 10.45 |  | 0
2014-08-24 | 0 | 0 | 10 |  | 0
2014-08-25 | 0 | 0 | 9.55 |  | 0
2014-08-26 | 0 | 0 | 9.1 |  | 0
2014-08-27 | 0 | 0 | 8.65 |  | 0
2014-08-28 | 0.4 | 0.04 | 8.24 |  | 0
2014-08-29 | 7.8 | 0.78 | 8.57 |  | 0
2014-08-30 | 3.6 | 0.36 | 8.48 |  | 0
2014-08-31 | 10.6 | 1.06 | 9.09 |  | 0
2014-09-01 | 3.2 | 0.32 | 8.96 |  | 0
2014-09-02 | 6.2 | 0.62 | 9.13 |  | 0
2014-09-03 | 0 | 0 | 8.68 |  | 0
2014-09-04 | 0 | 0 | 8.23 |  | 0
2014-09-05 | 0 | 0 | 7.78 |  | 0
2014-09-06 | 0 | 0 | 7.33 |  | 0
2014-09-07 | 0 | 0 | 6.88 |  | 0
2014-09-08 | 0 | 0 | 6.43 |  | 0
2014-09-09 | 0 | 0 | 5.98 |  | 0
2014-09-10 | 0 | 0 | 5.53 |  | 0
2014-09-11 | 0 | 0 | 5.08 |  | 0
2014-09-12 | 0 | 0 | 4.63 |  | 0
2014-09-13 | 0 | 0 | 4.18 |  | 0
2014-09-14 | 0 | 0 | 3.73 |  | 0
2014-09-15 | 0 | 0 | 3.28 |  | 0
2014-09-16 | 0 | 0 | 2.83 |  | 0
2014-09-17 | 0 | 0 | 2.38 |  | 0
2014-09-18 | 26.4 | 2.5 | 4.43 |  | 0
2014-09-19 | 0.4 | 0.04 | 4.02 |  | 0
2014-09-20 | 0 | 0 | 3.57 |  | 0
2014-09-21 | 2 | 0.2 | 3.32 |  | 0
2014-09-22 | 12.4 | 1.24 | 4.11 |  | 0
2014-09-23 | 29.4 | 2.5 | 6.16 |  | 0
2014-09-24 | 1.6 | 0.16 | 5.87 |  | 0
2014-09-25 | 0.6 | 0.06 | 5.48 |  | 0
2014-09-26 | 8.2 | 0.82 | 5.85 |  | 0
2014-09-27 | 0 | 0 | 5.4 |  | 0
2014-09-28 | 12.4 | 1.24 | 6.19 |  | 0
2014-09-29 | 5.6 | 0.56 | 6.3 |  | 0
2014-09-30 | 0 | 0 | 5.85 |  | 0
2014-10-01 | 0 | 0 | 5.4 |  | 0
2014-10-02 | 0 | 0 | 4.95 |  | 0
2014-10-03 | 57.8 | 2.5 | 7 |  | 0
2014-10-04 | 6 | 0.6 | 7.15 |  | 0
2014-10-05 | 9.2 | 0.92 | 7.62 |  | 0
2014-10-06 | 0.4 | 0.04 | 7.21 |  | 0
2014-10-07 | 0 | 0 | 6.76 |  | 0
2014-10-08 | 1.4 | 0.14 | 6.45 |  | 0
2014-10-09 | 1.8 | 0.18 | 6.18 |  | 0
2014-10-10 | 17.8 | 1.78 | 7.51 |  | 0
2014-10-11 | 15.4 | 1.54 | 8.6 |  | 0
2014-10-12 | 33 | 2.5 | 10.65 |  | 0
2014-10-13 | 31.4 | 2.5 | 12.7 |  | 0
2014-10-14 | 28.4 | 2.5 | 14.75 |  | 0
2014-10-15 | 6.4 | 0.64 | 14.94 |  | 0
2014-10-16 | 17.2 | 1.72 | 16.21 |  | 0
2014-10-17 | 27 | 2.5 | 18.26 |  | 0
2014-10-18 | 16.8 | 1.68 | 19.49 |  | 0
2014-10-19 | 46.2 | 2.5 | 21.54 |  | 0
2014-10-20 | 10.8 | 1.08 | 22.17 |  | 0
2014-10-21 | 40.2 | 2.5 | 24.22 |  | 0
2014-10-22 | 21.4 | 2.14 | 25.91 |  | 0
2014-10-23 | 9.4 | 0.94 | 26.4 |  | 0
2014-10-24 | 1.6 | 0.16 | 26.11 |  | 0
2014-10-25 | 21.8 | 2.18 | 27.84 |  | 0
2014-10-26 | 2.4 | 0.24 | 27.63 |  | 0
2014-10-27 | 33.6 | 2.5 | 29.68 |  | 0
2014-10-28 | 24.4 | 2.44 | 31.67 |  | 0
2014-10-29 | 7 | 0.7 | 31.92 |  | 0
2014-10-30 | 9 | 0.9 | 32.37 |  | 0
2014-10-31 | 15 | 1.5 | 33.42 |  | 0
2014-11-01 | 6.4 | 0.64 | 33.61 |  | 0
2014-11-02 | 37.6 | 2.5 | 35 |  | 0
2014-11-03 | 35.2 | 2.5 | 35 |  | 0
2014-11-04 | 9 | 0.9 | 35 |  | 0
2014-11-05 | 4.4 | 0.44 | 34.99 |  | 0
2014-11-06 | 20.2 | 2.02 | 35 |  | 0
2014-11-07 | 1.4 | 0.14 | 34.69 |  | 0
2014-11-08 | 34 | 2.5 | 35 |  | 0
2014-11-09 | 0 | 0 | 34.55 |  | 0
2014-11-10 | 0 | 0 | 34.1 |  | 0
2014-11-11 | 0 | 0 | 33.65 |  | 0
2014-11-12 | 0 | 0 | 33.2 |  | 0
2014-11-13 | 0 | 0 | 32.75 |  | 0
2014-11-14 | 0 | 0 | 32.3 |  | 0
2014-11-15 | 0 | 0 | 31.85 |  | 0
2014-11-16 | 0 | 0 | 31.4 |  | 0
2014-11-17 | 0 | 0 | 30.95 |  | 0
2014-11-18 | 0 | 0 | 30.5 |  | 0
2014-11-19 | 3.4 | 0.34 | 30.39 |  | 0
2014-11-20 | 29.4 | 2.5 | 32.44 |  | 0
2014-11-21 | 32.8 | 2.5 | 34.49 |  | 0
2014-11-22 | 25.6 | 2.5 | 35 |  | 0
2014-11-23 | 15.2 | 1.52 | 35 |  | 0
2014-11-24 | 60.6 | 2.5 | 35 |  | 0
2014-11-25 | 15 | 1.5 | 35 |  | 0
2014-11-26 | 43 | 2.5 | 35 |  | 0
2014-11-27 | 15 | 1.5 | 35 |  | 0
2014-11-28 | 0 | 0 | 34.55 |  | 0
2014-11-29 | 0 | 0 | 34.1 |  | 0
2014-11-30 | 0 | 0 | 33.65 |  | 0
2014-12-01 | 0 | 0 | 33.2 |  | 0
2014-12-02 | 0 | 0 | 32.75 |  | 0
2014-12-03 | 0 | 0 | 32.3 |  | 0
2014-12-04 | 1.2 | 0.12 | 31.97 |  | 0
2014-12-05 | 45.4 | 2.5 | 34.02 |  | 0
2014-12-06 | 0.8 | 0.08 | 33.65 |  | 0
2014-12-07 | 15.2 | 1.52 | 34.72 |  | 0
2014-12-08 | 48.6 | 2.5 | 35 |  | 0
2014-12-09 | 34.2 | 2.5 | 35 |  | 0
2014-12-10 | 4.4 | 0.44 | 34.99 |  | 0
2014-12-11 | 17.8 | 1.78 | 35 |  | 0
2014-12-12 | 1.4 | 0.14 | 34.69 |  | 0
2014-12-13 | 1 | 0.1 | 34.34 |  | 0
2014-12-14 | 0 | 0 | 33.89 |  | 0
2014-12-15 | 9 | 0.9 | 34.34 |  | 0
2014-12-16 | 20.2 | 2.02 | 35 |  | 0
2014-12-17 | 0.8 | 0.08 | 34.63 |  | 0
2014-12-18 | 24.6 | 2.46 | 35 |  | 0
2014-12-19 | 0 | 0 | 34.55 |  | 0
2014-12-20 | 0 | 0 | 34.1 |  | 0
2014-12-21 | 8.8 | 0.88 | 34.53 |  | 0
2014-12-22 | 11.6 | 1.16 | 35 |  | 0
2014-12-23 | 10 | 1 | 35 |  | 0
2014-12-24 | 2.2 | 0.22 | 34.77 |  | 0
2014-12-25 | 0.6 | 0.06 | 34.38 |  | 0
2014-12-26 | 10.2 | 1.02 | 34.95 |  | 0
2014-12-27 | 5.4 | 0.54 | 35 |  | 0
2014-12-28 | 0 | 0 | 34.55 |  | 0
2014-12-29 | 0 | 0 | 34.1 |  | 0
2014-12-30 | 0 | 0 | 33.65 |  | 0
2014-12-31 | 0 | 0 | 33.2 |  | 0
2015-01-01 | 7.8 | 0.78 | 33.53 |  | 0
2015-01-02 | 1 | 0.1 | 33.18 |  | 0
2015-01-03 | 13.4 | 1.34 | 34.07 |  | 0
2015-01-04 | 64.2 | 2.5 | 35 |  | 0
2015-01-05 | 32.2 | 2.5 | 35 |  | 0
2015-01-06 | 2.8 | 0.28 | 34.83 |  | 0
2015-01-07 | 0 | 0 | 34.38 |  | 0
2015-01-08 | 0 | 0 | 33.93 |  | 0
2015-01-09 | 0.8 | 0.08 | 33.56 |  | 0
2015-01-10 | 0 | 0 | 33.11 |  | 0
2015-01-11 | 0 | 0 | 32.66 |  | 0
2015-01-12 | 0 | 0 | 32.21 |  | 0
2015-01-13 | 0 | 0 | 31.76 |  | 0
2015-01-14 | 0.4 | 0.04 | 31.35 |  | 0
2015-01-15 | 35.4 | 2.5 | 33.4 |  | 0
2015-01-16 | 6 | 0.6 | 33.55 |  | 0
2015-01-17 | 20.4 | 2.04 | 35 |  | 0
2015-01-18 | 16.6 | 1.66 | 35 |  | 0
2015-01-19 | 2.6 | 0.26 | 34.81 |  | 0
2015-01-20 | 0.4 | 0.04 | 34.4 |  | 0
2015-01-21 | 18.4 | 1.84 | 35 |  | 0
2015-01-22 | 14 | 1.4 | 35 |  | 0
2015-01-23 | 90.8 | 2.5 | 35 |  | 0
2015-01-24 | 40 | 2.5 | 35 |  | 0
2015-01-25 | 1.8 | 0.18 | 34.73 |  | 0
2015-01-26 | 2.8 | 0.28 | 34.56 |  | 0
2015-01-27 | 2.8 | 0.28 | 34.39 |  | 0
2015-01-28 | 0 | 0 | 33.94 |  | 0
2015-01-29 | 0 | 0 | 33.49 |  | 0
2015-01-30 | 0.6 | 0.06 | 33.1 |  | 0
2015-01-31 | 5.8 | 0.58 | 33.23 |  | 0
2015-02-01 | 8 | 0.8 | 33.58 |  | 0
2015-02-02 | 27 | 2.5 | 35 |  | 0
2015-02-03 | 0.6 | 0.06 | 34.61 |  | 0
2015-02-04 | 36 | 2.5 | 35 |  | 0
2015-02-05 | 27.2 | 2.5 | 35 |  | 0
2015-02-06 | 28.2 | 2.5 | 35 |  | 0
2015-02-07 | 39.2 | 2.5 | 35 |  | 0
2015-02-08 | 6.6 | 0.66 | 35 |  | 0
2015-02-09 | 3.2 | 0.32 | 34.87 |  | 0
2015-02-10 | 0.2 | 0.02 | 34.44 |  | 0
2015-02-11 | 19.6 | 1.96 | 35 |  | 0
2015-02-12 | 30.4 | 2.5 | 35 |  | 0
2015-02-13 | 19 | 1.9 | 35 |  | 0
2015-02-14 | 0.2 | 0.02 | 34.57 |  | 0
2015-02-15 | 0 | 0 | 34.12 |  | 0
2015-02-16 | 0 | 0 | 33.67 |  | 0
2015-02-17 | 0 | 0 | 33.22 |  | 0
2015-02-18 | 4 | 0.4 | 33.17 |  | 0
2015-02-19 | 11 | 1.1 | 33.82 |  | 0
2015-02-20 | 0.4 | 0.04 | 33.41 |  | 0
2015-02-21 | 0 | 0 | 32.96 |  | 0
2015-02-22 | 0 | 0 | 32.51 |  | 0
2015-02-23 | 0 | 0 | 32.06 |  | 0
2015-02-24 | 0.2 | 0.02 | 31.63 |  | 0
2015-02-25 | 4.6 | 0.46 | 31.64 |  | 0
2015-02-26 | 8.8 | 0.88 | 32.07 |  | 0
2015-02-27 | 0.4 | 0.04 | 31.66 |  | 0
2015-02-28 | 0 | 0 | 31.21 |  | 0
2015-03-01 | 1.2 | 0.12 | 30.88 |  | 0
2015-03-02 | 0 | 0 | 30.43 |  | 0
2015-03-03 | 0 | 0 | 29.98 |  | 0
2015-03-04 | 0.4 | 0.04 | 29.57 |  | 0
2015-03-05 | 1.8 | 0.18 | 29.3 |  | 0
2015-03-06 | 0.8 | 0.08 | 28.93 |  | 0
2015-03-07 | 0 | 0 | 28.48 |  | 0
2015-03-08 | 0.4 | 0.04 | 28.07 |  | 0
2015-03-09 | 0.4 | 0.04 | 27.66 |  | 0
2015-03-10 | 2.8 | 0.28 | 27.49 |  | 0
2015-03-11 | 13.6 | 1.36 | 28.4 |  | 0
2015-03-12 | 8.6 | 0.86 | 28.81 |  | 0
2015-03-13 | 17.4 | 1.74 | 30.1 |  | 0
2015-03-14 | 0.6 | 0.06 | 29.71 |  | 0
2015-03-15 | 0 | 0 | 29.26 |  | 0
2015-03-16 | 0 | 0 | 28.81 |  | 0
2015-03-17 | 0 | 0 | 28.36 |  | 0
2015-03-18 | 31 | 2.5 | 30.41 |  | 0
2015-03-19 | 35.4 | 2.5 | 32.46 |  | 0
2015-03-20 | 28.6 | 2.5 | 34.51 |  | 0
2015-03-21 | 0 | 0 | 34.06 |  | 0
2015-03-22 | 7 | 0.7 | 34.31 |  | 0
2015-03-23 | 9.6 | 0.96 | 34.82 |  | 0
2015-03-24 | 18.2 | 1.82 | 35 |  | 0
2015-03-25 | 104.4 | 2.5 | 35 |  | 0
2015-03-26 | 33.2 | 2.5 | 35 |  | 0
2015-03-27 | 26.2 | 2.5 | 35 |  | 0
2015-03-28 | 68.8 | 2.5 | 35 |  | 0
2015-03-29 | 10 | 1 | 35 |  | 0
2015-03-30 | 37.7 | 2.5 | 35 |  | 0
2015-03-31 | 11.6 | 1.16 | 35 |  | 0
2015-04-01 | 0 | 0 | 34.55 |  | 0
2015-04-02 | 33.7 | 2.5 | 35 |  | 0
2015-04-03 | 9 | 0.9 | 35 |  | 0
2015-04-04 | 8.4 | 0.84 | 35 |  | 0
2015-04-05 | 0.6 | 0.06 | 34.61 |  | 0
2015-04-06 | 0 | 0 | 34.16 |  | 0
2015-04-07 | 0 | 0 | 33.71 |  | 0
2015-04-08 | 0 | 0 | 33.26 |  | 0
2015-04-09 | 3.2 | 0.32 | 33.13 |  | 0
2015-04-10 | 40.2 | 2.5 | 35 |  | 0
2015-04-11 | 9.2 | 0.92 | 35 |  | 0
2015-04-12 | 24.4 | 2.44 | 35 |  | 0
2015-04-13 | 16.2 | 1.62 | 35 |  | 0
2015-04-14 | 1.5 | 0.15 | 34.7 |  | 0
2015-04-15 | 37.2 | 2.5 | 35 |  | 0
2015-04-16 | 3 | 0.3 | 34.85 |  | 0
2015-04-17 | 0 | 0 | 34.4 |  | 0
2015-04-18 | 0 | 0 | 33.95 |  | 0
2015-04-19 | 0 | 0 | 33.5 |  | 0
2015-04-20 | 1.1 | 0.11 | 33.16 |  | 0
2015-04-21 | 0.4 | 0.04 | 32.75 |  | 0
2015-04-22 | 8.2 | 0.82 | 33.12 |  | 0
2015-04-23 | 8.4 | 0.84 | 33.51 |  | 0
2015-04-24 | 1.8 | 0.18 | 33.24 |  | 0
2015-04-25 | 0 | 0 | 32.79 |  | 0
2015-04-26 | 4.2 | 0.42 | 32.76 |  | 0
2015-04-27 | 22.4 | 2.24 | 34.55 |  | 0
2015-04-28 | 15.4 | 1.54 | 35 |  | 0
2015-04-29 | 27.6 | 2.5 | 35 |  | 0
2015-04-30 | 4.8 | 0.48 | 35 |  | 0
2015-05-01 | 0.8 | 0.08 | 34.63 |  | 0
2015-05-02 | 0 | 0 | 34.18 |  | 0
2015-05-03 | 0 | 0 | 33.73 |  | 0
2015-05-04 | 19.8 | 1.98 | 35 |  | 0
2015-05-05 | 0.4 | 0.04 | 34.59 |  | 0
2015-05-06 | 0 | 0 | 34.14 |  | 0
2015-05-07 | 0 | 0 | 33.69 |  | 0
2015-05-08 | 0 | 0 | 33.24 |  | 0
2015-05-09 | 0 | 0 | 32.79 |  | 0
2015-05-10 | 0.4 | 0.04 | 32.38 |  | 0
2015-05-11 | 0 | 0 | 31.93 |  | 0
2015-05-12 | 0 | 0 | 31.48 |  | 0
2015-05-13 | 0 | 0 | 31.03 |  | 0
2015-05-14 | 0 | 0 | 30.58 |  | 0
2015-05-15 | 0 | 0 | 30.13 |  | 0
2015-05-16 | 0.2 | 0.02 | 29.7 |  | 0
2015-05-17 | 0 | 0 | 29.25 |  | 0
2015-05-18 | 0 | 0 | 28.8 |  | 0
2015-05-19 | 0 | 0 | 28.35 |  | 0
2015-05-20 | 0 | 0 | 27.9 |  | 0
2015-05-21 | 0 | 0 | 27.45 |  | 0
2015-05-22 | 0.2 | 0.02 | 27.02 |  | 0
2015-05-23 | 0.2 | 0.02 | 26.59 |  | 0
2015-05-24 | 0 | 0 | 26.14 |  | 0
2015-05-25 | 0 | 0 | 25.69 |  | 0
2015-05-26 | 0 | 0 | 25.24 |  | 0
2015-05-27 | 0 | 0 | 24.79 |  | 0
2015-05-28 | 0 | 0 | 24.34 |  | 0
2015-05-29 | 0 | 0 | 23.89 |  | 0
2015-05-30 | 0 | 0 | 23.44 |  | 0
2015-05-31 | 0 | 0 | 22.99 |  | 0
2015-06-01 | 7.4 | 0.74 | 23.28 |  | 0
2015-06-02 | 2.8 | 0.28 | 23.11 |  | 0
2015-06-03 | 0 | 0 | 22.66 |  | 0
2015-06-04 | 0 | 0 | 22.21 |  | 0
2015-06-05 | 0 | 0 | 21.76 |  | 0
2015-06-06 | 0 | 0 | 21.31 |  | 0
2015-06-07 | 0 | 0 | 20.86 |  | 0
2015-06-08 | 0 | 0 | 20.41 |  | 0
2015-06-09 | 0 | 0 | 19.96 |  | 0
2015-06-10 | 0 | 0 | 19.51 |  | 0
2015-06-11 | 0 | 0 | 19.06 |  | 0
2015-06-12 | 0 | 0 | 18.61 |  | 0
2015-06-13 | 0 | 0 | 18.16 |  | 0
2015-06-14 | 0 | 0 | 17.71 |  | 0
2015-06-15 | 0 | 0 | 17.26 |  | 0
2015-06-16 | 0 | 0 | 16.81 |  | 0
2015-06-17 | 0 | 0 | 16.36 |  | 0
2015-06-18 | 7 | 0.7 | 16.61 |  | 0
2015-06-19 | 0 | 0 | 16.16 |  | 0
2015-06-20 | 0 | 0 | 15.71 |  | 0
2015-06-21 | 0 | 0 | 15.26 |  | 0
2015-06-22 | 0 | 0 | 14.81 |  | 0
2015-06-23 | 1.4 | 0.14 | 14.5 |  | 0
2015-06-24 | 13.4 | 1.34 | 15.39 |  | 0
2015-06-25 | 4 | 0.4 | 15.34 |  | 0
2015-06-26 | 0 | 0 | 14.89 |  | 0
2015-06-27 | 0 | 0 | 14.44 |  | 0
2015-06-28 | 0 | 0 | 13.99 |  | 0
2015-06-29 | 0 | 0 | 13.54 |  | 0
2015-06-30 | 0 | 0 | 13.09 |  | 0
2015-07-01 | 0 | 0 | 12.64 |  | 0
2015-07-02 | 0 | 0 | 12.19 |  | 0
2015-07-03 | 0 | 0 | 11.74 |  | 0
2015-07-04 | 0 | 0 | 11.29 |  | 0
2015-07-05 | 0 | 0 | 10.84 |  | 0
2015-07-06 | 0 | 0 | 10.39 |  | 0
2015-07-07 | 0.2 | 0.02 | 9.96 |  | 0
2015-07-08 | 0 | 0 | 9.51 |  | 0
2015-07-09 | 1 | 0.1 | 9.16 |  | 0
2015-07-10 | 1.2 | 0.12 | 8.83 |  | 0
2015-07-11 | 2.4 | 0.24 | 8.62 |  | 0
2015-07-12 | 4 | 0.4 | 8.57 |  | 0
2015-07-13 | 0 | 0 | 8.12 |  | 0
2015-07-14 | 0 | 0 | 7.67 |  | 0
2015-07-15 | 0 | 0 | 7.22 |  | 0
2015-07-16 | 0 | 0 | 6.77 |  | 0
2015-07-17 | 0 | 0 | 6.32 |  | 0
2015-07-18 | 0 | 0 | 5.87 |  | 0
2015-07-19 | 0 | 0 | 5.42 |  | 0
2015-07-20 | 0.6 | 0.06 | 5.03 |  | 0
2015-07-21 | 0 | 0 | 4.58 |  | 0
2015-07-22 | 0 | 0 | 4.13 |  | 0
2015-07-23 | 8.4 | 0.84 | 4.52 |  | 0
2015-07-24 | 4 | 0.4 | 4.47 |  | 0
2015-07-25 | 4.2 | 0.42 | 4.44 |  | 0
2015-07-26 | 0 | 0 | 3.99 |  | 0
2015-07-27 | 0 | 0 | 3.54 |  | 0
2015-07-28 | 0 | 0 | 3.09 |  | 0
2015-07-29 | 0 | 0 | 2.64 |  | 0
2015-07-30 | 0 | 0 | 2.19 |  | 0
2015-07-31 | 0 | 0 | 1.74 |  | 0
2015-08-01 | 0 | 0 | 1.29 |  | 0
2015-08-02 | 0 | 0 | 0.84 |  | 0
2015-08-03 | 0 | 0 | 0.39 |  | 0
2015-08-04 | 0 | 0 | 0 | 100% | 1
2015-08-05 | 0 | 0 | 0 | 100% | 1
2015-08-06 | 3.2 | 0.32 | 0 | 100% | 1
2015-08-07 | 14.6 | 1.46 | 1.01 |  | 0
2015-08-08 | 24.4 | 2.44 | 3 |  | 0
2015-08-09 | 1.8 | 0.18 | 2.73 |  | 0
2015-08-10 | 0 | 0 | 2.28 |  | 0
2015-08-11 | 0 | 0 | 1.83 |  | 0
2015-08-12 | 0 | 0 | 1.38 |  | 0
2015-08-13 | 0 | 0 | 0.93 |  | 0
2015-08-14 | 0 | 0 | 0.48 |  | 0
2015-08-15 | 0 | 0 | 0.03 |  | 0
2015-08-16 | 0 | 0 | 0 | 100% | 1
2015-08-17 | 0 | 0 | 0 | 100% | 1
2015-08-18 | 0 | 0 | 0 | 100% | 1
2015-08-19 | 0 | 0 | 0 | 100% | 1
2015-08-20 | 0 | 0 | 0 | 100% | 1
2015-08-21 | 0 | 0 | 0 | 100% | 1
2015-08-22 | 0 | 0 | 0 | 100% | 1
2015-08-23 | 0 | 0 | 0 | 100% | 1
2015-08-24 | 0 | 0 | 0 | 100% | 1
2015-08-25 | 0 | 0 | 0 | 100% | 1
2015-08-26 | 0 | 0 | 0 | 100% | 1
2015-08-27 | 2.8 | 0.28 | 0 | 100% | 1
2015-08-28 | 10.4 | 1.04 | 0.59 |  | 0
2015-08-29 | 33.4 | 2.5 | 2.64 |  | 0
2015-08-30 | 26 | 2.5 | 4.69 |  | 0
2015-08-31 | 6 | 0.6 | 4.84 |  | 0
2015-09-01 | 15.8 | 1.58 | 5.97 |  | 0
2015-09-02 | 0.8 | 0.08 | 5.6 |  | 0
2015-09-03 | 2.4 | 0.24 | 5.39 |  | 0
2015-09-04 | 0 | 0 | 4.94 |  | 0
2015-09-05 | 1.6 | 0.16 | 4.65 |  | 0
2015-09-06 | 0 | 0 | 4.2 |  | 0
2015-09-07 | 29.6 | 2.5 | 6.25 |  | 0
2015-09-08 | 13 | 1.3 | 7.1 |  | 0
2015-09-09 | 1.4 | 0.14 | 6.79 |  | 0
2015-09-10 | 0 | 0 | 6.34 |  | 0
2015-09-11 | 0 | 0 | 5.89 |  | 0
2015-09-12 | 0 | 0 | 5.44 |  | 0
2015-09-13 | 0 | 0 | 4.99 |  | 0
2015-09-14 | 0 | 0 | 4.54 |  | 0
2015-09-15 | 2 | 0.2 | 4.29 |  | 0
2015-09-16 | 4 | 0.4 | 4.24 |  | 0
2015-09-17 | 2.8 | 0.28 | 4.07 |  | 0
2015-09-18 | 46.4 | 2.5 | 6.12 |  | 0
2015-09-19 | 86.8 | 2.5 | 8.17 |  | 0
2015-09-20 | 1.4 | 0.14 | 7.86 |  | 0
2015-09-21 | 4.2 | 0.42 | 7.83 |  | 0
2015-09-22 | 39.8 | 2.5 | 9.88 |  | 0
2015-09-23 | 29.8 | 2.5 | 11.93 |  | 0
2015-09-24 | 11.8 | 1.18 | 12.66 |  | 0
2015-09-25 | 1.6 | 0.16 | 12.37 |  | 0
2015-09-26 | 0 | 0 | 11.92 |  | 0
2015-09-27 | 0 | 0 | 11.47 |  | 0
2015-09-28 | 0 | 0 | 11.02 |  | 0
2015-09-29 | 0 | 0 | 10.57 |  | 0
2015-09-30 | 0 | 0 | 10.12 |  | 0
2015-10-01 | 0 | 0 | 9.67 |  | 0
2015-10-02 | 0 | 0 | 9.22 |  | 0
2015-10-03 | 0 | 0 | 8.77 |  | 0
2015-10-04 | 0 | 0 | 8.32 |  | 0
2015-10-05 | 0 | 0 | 7.87 |  | 0
2015-10-06 | 4 | 0.4 | 7.82 |  | 0
2015-10-07 | 15.6 | 1.56 | 8.93 |  | 0
2015-10-08 | 9.2 | 0.92 | 9.4 |  | 0
2015-10-09 | 26.4 | 2.5 | 11.45 |  | 0
2015-10-10 | 27 | 2.5 | 13.5 |  | 0
2015-10-11 | 37.6 | 2.5 | 15.55 |  | 0
2015-10-12 | 0.8 | 0.08 | 15.18 |  | 0
2015-10-13 | 0.6 | 0.06 | 14.79 |  | 0
2015-10-14 | 0 | 0 | 14.34 |  | 0
2015-10-15 | 0 | 0 | 13.89 |  | 0
2015-10-16 | 14.2 | 1.42 | 14.86 |  | 0
2015-10-17 | 6.4 | 0.64 | 15.05 |  | 0
2015-10-18 | 23.4 | 2.34 | 16.94 |  | 0
2015-10-19 | 0.6 | 0.06 | 16.55 |  | 0
2015-10-20 | 10.2 | 1.02 | 17.12 |  | 0
2015-10-21 | 4 | 0.4 | 17.07 |  | 0
2015-10-22 | 9.8 | 0.98 | 17.6 |  | 0
2015-10-23 | 0 | 0 | 17.15 |  | 0
2015-10-24 | 5.8 | 0.58 | 17.28 |  | 0
2015-10-25 | 4 | 0.4 | 17.23 |  | 0
2015-10-26 | 0 | 0 | 16.78 |  | 0
2015-10-27 | 6.8 | 0.68 | 17.01 |  | 0
2015-10-28 | 39 | 2.5 | 19.06 |  | 0
2015-10-29 | 40.6 | 2.5 | 21.11 |  | 0
2015-10-30 | 35.4 | 2.5 | 23.16 |  | 0
2015-10-31 | 21.2 | 2.12 | 24.83 |  | 0
2015-11-01 | 1.2 | 0.12 | 24.5 |  | 0
2015-11-02 | 0 | 0 | 24.05 |  | 0
2015-11-03 | 0 | 0 | 23.6 |  | 0
2015-11-04 | 3.4 | 0.34 | 23.49 |  | 0
2015-11-05 | 6 | 0.6 | 23.64 |  | 0
2015-11-06 | 44.2 | 2.5 | 25.69 |  | 0
2015-11-07 | 2.2 | 0.22 | 25.46 |  | 0
2015-11-08 | 1.6 | 0.16 | 25.17 |  | 0
2015-11-09 | 0 | 0 | 24.72 |  | 0
2015-11-10 | 20.5 | 2.05 | 26.32 |  | 0
2015-11-11 | 18.8 | 1.88 | 27.75 |  | 0
2015-11-12 | 59 | 2.5 | 29.8 |  | 0
2015-11-13 | 11.4 | 1.14 | 30.49 |  | 0
2015-11-14 | 0.6 | 0.06 | 30.1 |  | 0
2015-11-15 | 6 | 0.6 | 30.25 |  | 0
2015-11-16 | 55.4 | 2.5 | 32.3 |  | 0
2015-11-17 | 6.2 | 0.62 | 32.47 |  | 0
2015-11-18 | 0 | 0 | 32.02 |  | 0
2015-11-19 | 0 | 0 | 31.57 |  | 0
2015-11-20 | 0 | 0 | 31.12 |  | 0
2015-11-21 | 0 | 0 | 30.67 |  | 0
2015-11-22 | 0 | 0 | 30.22 |  | 0
2015-11-23 | 0 | 0 | 29.77 |  | 0
2015-11-24 | 0 | 0 | 29.32 |  | 0
2015-11-25 | 0 | 0 | 28.87 |  | 0
2015-11-26 | 0 | 0 | 28.42 |  | 0
2015-11-27 | 0 | 0 | 27.97 |  | 0
2015-11-28 | 0 | 0 | 27.52 |  | 0
2015-11-29 | 0 | 0 | 27.07 |  | 0
2015-11-30 | 13 | 1.3 | 27.92 |  | 0
2015-12-01 | 34.6 | 2.5 | 29.97 |  | 0
2015-12-02 | 27.4 | 2.5 | 32.02 |  | 0
2015-12-03 | 32.6 | 2.5 | 34.07 |  | 0
2015-12-04 | 27.2 | 2.5 | 35 |  | 0
2015-12-05 | 33.8 | 2.5 | 35 |  | 0
2015-12-06 | 22.4 | 2.24 | 35 |  | 0
2015-12-07 | 37.2 | 2.5 | 35 |  | 0
2015-12-08 | 27 | 2.5 | 35 |  | 0
2015-12-09 | 4.8 | 0.48 | 35 |  | 0
2015-12-10 | 12.2 | 1.22 | 35 |  | 0
2015-12-11 | 3.4 | 0.34 | 34.89 |  | 0
2015-12-12 | 23.8 | 2.38 | 35 |  | 0
2015-12-13 | 0 | 0 | 34.55 |  | 0
2015-12-14 | 2.4 | 0.24 | 34.34 |  | 0
2015-12-15 | 3 | 0.3 | 34.19 |  | 0
2015-12-16 | 2.2 | 0.22 | 33.96 |  | 0
2015-12-17 | 21.8 | 2.18 | 35 |  | 0
2015-12-18 | 25.5 | 2.5 | 35 |  | 0
2015-12-19 | 31.8 | 2.5 | 35 |  | 0
2015-12-20 | 22.6 | 2.26 | 35 |  | 0
2015-12-21 | 9 | 0.9 | 35 |  | 0
2015-12-22 | 35.8 | 2.5 | 35 |  | 0
2015-12-23 | 9.4 | 0.94 | 35 |  | 0
2015-12-24 | 0 | 0 | 34.55 |  | 0
2015-12-25 | 0 | 0 | 34.1 |  | 0
2015-12-26 | 26.2 | 2.5 | 35 |  | 0
2015-12-27 | 1.6 | 0.16 | 34.71 |  | 0
2015-12-28 | 0.2 | 0.02 | 34.28 |  | 0
2015-12-29 | 0 | 0 | 33.83 |  | 0
2015-12-30 | 0 | 0 | 33.38 |  | 0
2015-12-31 | 0 | 0 | 32.93 |  | 0

## Overall Cost
Cost over 5 years
Area of roof | 350
Storage Tank | 9625 |  | Satifaction | Cost
Catchment Tank | 900 | Minimum Satifaction | 1% | 130000
Shipping in water | 1875 | Minimum Satifaction | 99% | 25000
Piping Costs |  | Cost to ship in water
Cost | 612.0662 | 100000
Tower
Cost | 5300.1499
Generator |  | Solar Panels
Pump | 1250 | Pump | 1250
Ozone | 4000 | Ozone | 4000
UV | 750 | UV | 750
UV bulbs | 450 | UV bulbs | 450
Filters | 335 | Filters | 335
Replacement filters | 7400 | Replacement filters | 7400
Battery | 390 | Panels | 6500
Cost of Fuel | 4971.8274 | Inverter | 2369
Cost of oil | 250 | Batteries | 1950
Cost of Generator | 3250
Total | 41709.0434 | Total | 43666.216
Cost Satisfaction |  | Cost Satisfaction
93.88% |  | 92.4%

## Experimental Pump
| Initial Water Level | Height of Filter Level | Height difference, h | Pressure (pgh) | Collected Volume | Collected Volume | Time | Time | Average Flow Rate | Average Flow Rate | Velocity | Pipe Diameter | Pipe Radius
Trial: | [m] | [m] | [m] | [Pa] | [mL] | [L] | [sec] | [min] | [L/min] | [m^3/s] | [m/s] | [m] | [m]
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.005
1 | 0 | 0.3 | 0.3 | 2943 | 250 | 0.25 | 39 | 0.65 | 0.38462 | 6.4103e-06 | 0.081618
2 | 0 | 0.4 | 0.4 | 3924 | 250 | 0.25 | 32.25 | 0.5375 | 0.46512 | 7.7519e-06 | 0.098701
3 | 0 | 0.8 | 0.8 | 7848 | 250 | 0.25 | 21 | 0.35 | 0.71429 | 1.1905e-05 | 0.15158
4 | 0 | 1.1 | 1.1 | 10791 | 250 | 0.25 | 17.3 | 0.28833 | 0.86705 | 1.4451e-05 | 0.18399
5 | 0 | 1.3 | 1.3 | 12753 | 250 | 0.25 | 15.8 | 0.26333 | 0.94937 | 1.5823e-05 | 0.20146
Cf Value = 3E-5

## Final Values
Design Consumption | Avg per day | 450 | L/day
Subsystem | Component | Input Required | Notes
Rain Water Collection | Roof Catchment | Whole Roof
| Additional Catchment | None | m^2
| Collection Tank | 2.5 | m^3
Storage | Storage Tank | 35 | m^3
| Location x | 2 | m
| Location y | 9 | m
| Tower | 6.5 | m
Pump | Choice | Pump B
Filter | Path | From tower to house
| Components | All filters
Disinfection | UV | 50 W UV System
| Chemical | Ozone
Power System | Power Strategy | Solar
| Number of batteries | 5
| Solar Panel Model | HES-260
| Number of Panels | 13
| Inverter | 2.8 kW DC-AC Inverter